## DASHBOARD
DISTRIBUTION SYSTEM RELIABILITY CASES
This chart isn't available in your version of Excel. Editing this shape or saving this workbook into a different file format will permanently break the chart.
Base Case has an energy loss of 520,996.02kWh. As cases progress, more disconnect switches are added to the system, with Case 8 having the least amount of energy loss of 220,638.07 kWh.
This chart isn't available in your version of Excel. Editing this shape or saving this workbook into a different file format will permanently break the chart.
Although Case 8 has the least energy lost, it is not the most economical or cost effective for the business as it only saves 37544.74kWh. The best scenario would be the one with the highest energy saved per switch so that ROI will be quicker. Case 3 is the best option since it can save 70768.87kWh per switch, there are a total of three switches.

## DATA AND SCENARIO
Component | No. of Customer/s | Load Connected (kW) | Component | ʎ(f/yr) | r(hrs) | Case | Scenario | Switching Time
M1 | 34855 | 19085.83 | A-B | 0.6 | 2.5 | Base Case | Base Scenario | 0.333hrs
M2 | 1 | 2585.36 | B-C | 0.4 | 2 | Case01 | Switch@ B-C
M3 | 7899 | 2575.86 | C-D | 0.4 | 2 | Case 02 | Case 01 & Switch @ C-D
M4 | 8746 | 9494.65 | B-E | 0.3 | 4 | Case03 | Case 02 & Switch @ B-E
M5 | 11141 | 3741.32 | E-F | 0.3 | 3 | Case04 | Case 03 & Switch @ E-F
M6 | 7223 | 2795.99 | F-G | 0.6 | 2.5 | Case05 | Case 04 & Switch @ F-G
M7 | 32947 | 9850.62 | F-H | 0.5 | 3 | Case06 | Case 05 & Switch @ F-H
M8 | 1 | 1710.77 | H-I | 0.3 | 3 | Case07 | Case 06 & Switch @ H-I
|  |  | I-J | 0.2 | 1 | Case08 | Case 07 & Switch @ I-K
|  |  | I-K | 0.3 | 2.5

## RELIABILITY INDICES
Base Case |  |  | LOAD Pt. M1 |  |  | LOAD Pt. M2 |  |  | LOAD Pt. M3 |  |  | LOAD Pt. M4 |  |  | LOAD Pt. M5 |  |  | LOAD Pt. M6 |  |  | LOAD Pt. M7 |  |  | LOAD Pt. M8
| COMPONENT FAILURE |  | ʎ (f/yr) | r (hrs) | U (hours/year) | ʎ (f/yr) | r (hrs) | U (hours/year) | ʎ (f/yr) | r (hrs) | U (hours/year) | ʎ (f/yr) | r (hrs) | U (hours/year) | ʎ (f/yr) | r (hrs) | U (hours/year) | ʎ (f/yr) | r (hrs) | U (hours/year) | ʎ (f/yr) | r (hrs) | U (hours/year) | ʎ (f/yr) | r (hrs) | U (hours/year)
| MAIN | A-B | 0.6 | 2.5 | 1.5 | 0.6 | 2.5 | 1.5 | 0.6 | 2.5 | 1.5 | 0.6 | 2.5 | 1.5 | 0.6 | 2.5 | 1.5 | 0.6 | 2.5 | 1.5 | 0.6 | 2.5 | 1.5 | 0.6 | 2.5 | 1.5
|  | B-C | 0.4 | 2 | 0.8 | 0.4 | 2 | 0.8 | 0.4 | 2 | 0.8 | 0.4 | 2 | 0.8 | 0.4 | 2 | 0.8 | 0.4 | 2 | 0.8 | 0.4 | 2 | 0.8 | 0.4 | 2 | 0.8
|  | C-D | 0.4 | 2 | 0.8 | 0.4 | 2 | 0.8 | 0.4 | 2 | 0.8 | 0.4 | 2 | 0.8 | 0.4 | 2 | 0.8 | 0.4 | 2 | 0.8 | 0.4 | 2 | 0.8 | 0.4 | 2 | 0.8
|  | B-E | 0.3 | 4 | 1.2 | 0.3 | 4 | 1.2 | 0.3 | 4 | 1.2 | 0.3 | 4 | 1.2 | 0.3 | 4 | 1.2 | 0.3 | 4 | 1.2 | 0.3 | 4 | 1.2 | 0.3 | 4 | 1.2
|  | E-F | 0.3 | 3 | 0.9 | 0.3 | 3 | 0.9 | 0.3 | 3 | 0.9 | 0.3 | 3 | 0.9 | 0.3 | 3 | 0.9 | 0.3 | 3 | 0.9 | 0.3 | 3 | 0.9 | 0.3 | 3 | 0.9
|  | F-G | 0.6 | 2.5 | 1.5 | 0.6 | 2.5 | 1.5 | 0.6 | 2.5 | 1.5 | 0.6 | 2.5 | 1.5 | 0.6 | 2.5 | 1.5 | 0.6 | 2.5 | 1.5 | 0.6 | 2.5 | 1.5 | 0.6 | 2.5 | 1.5
|  | F-H | 0.5 | 3 | 1.5 | 0.5 | 3 | 1.5 | 0.5 | 3 | 1.5 | 0.5 | 3 | 1.5 | 0.5 | 3 | 1.5 | 0.5 | 3 | 1.5 | 0.5 | 3 | 1.5 | 0.5 | 3 | 1.5
|  | H-I | 0.3 | 3 | 0.9 | 0.3 | 3 | 0.9 | 0.3 | 3 | 0.9 | 0.3 | 3 | 0.9 | 0.3 | 3 | 0.9 | 0.3 | 3 | 0.9 | 0.3 | 3 | 0.9 | 0.3 | 3 | 0.9
|  | I-J | 0.2 | 1 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 1 | 0.2
|  | I-K | 0.3 | 2.5 | 0.75 | 0.3 | 2.5 | 0.75 | 0.3 | 2.5 | 0.75 | 0.3 | 2.5 | 0.75 | 0.3 | 2.5 | 0.75 | 0.3 | 2.5 | 0.75 | 0.3 | 2.5 | 0.75 | 0.3 | 2.5 | 0.75
|  | TOTAL | 3.9 | 2.5769 | 10.05 | 3.9 | 2.5769 | 10.05 | 3.9 | 2.5769 | 10.05 | 3.9 | 2.5769 | 10.05 | 3.9 | 2.5769 | 10.05 | 3.9 | 2.5769 | 10.05 | 3.9 | 2.5769 | 10.05 | 3.9 | 2.5769 | 10.05
Case 1 |  |  | LOAD Pt. M1 |  |  | LOAD Pt. M2 |  |  | LOAD Pt. M3 |  |  | LOAD Pt. M4 |  |  | LOAD Pt. M5 |  |  | LOAD Pt. M6 |  |  | LOAD Pt. M7 |  |  | LOAD Pt. M8
| COMPONENT FAILURE |  | ʎ (f/yr) | r (hrs) | U (hours/year) | ʎ (f/yr) | r (hrs) | U (hours/year) | ʎ (f/yr) | r (hrs) | U (hours/year) | ʎ (f/yr) | r (hrs) | U (hours/year) | ʎ (f/yr) | r (hrs) | U (hours/year) | ʎ (f/yr) | r (hrs) | U (hours/year) | ʎ (f/yr) | r (hrs) | U (hours/year) | ʎ (f/yr) | r (hrs) | U (hours/year)
| MAIN | A-B | 0.6 | 2.5 | 1.5 | 0.6 | 2.5 | 1.5 | 0.6 | 2.5 | 1.5 | 0.6 | 2.5 | 1.5 | 0.6 | 2.5 | 1.5 | 0.6 | 2.5 | 1.5 | 0.6 | 2.5 | 1.5 | 0.6 | 2.5 | 1.5
|  | B-C | 0.4 | 0.333 | 0.1332 | 0.4 | 2 | 0.8 | 0.4 | 2 | 0.8 | 0.4 | 0.333 | 0.1332 | 0.4 | 0.333 | 0.1332 | 0.4 | 0.333 | 0.1332 | 0.4 | 0.333 | 0.1332 | 0.4 | 0.333 | 0.1332
|  | C-D | 0.4 | 0.333 | 0.1332 | 0.4 | 2 | 0.8 | 0.4 | 2 | 0.8 | 0.4 | 0.333 | 0.1332 | 0.4 | 0.333 | 0.1332 | 0.4 | 0.333 | 0.1332 | 0.4 | 0.333 | 0.1332 | 0.4 | 0.333 | 0.1332
|  | B-E | 0.3 | 4 | 1.2 | 0.3 | 4 | 1.2 | 0.3 | 4 | 1.2 | 0.3 | 4 | 1.2 | 0.3 | 4 | 1.2 | 0.3 | 4 | 1.2 | 0.3 | 4 | 1.2 | 0.3 | 4 | 1.2
|  | E-F | 0.3 | 3 | 0.9 | 0.3 | 3 | 0.9 | 0.3 | 3 | 0.9 | 0.3 | 3 | 0.9 | 0.3 | 3 | 0.9 | 0.3 | 3 | 0.9 | 0.3 | 3 | 0.9 | 0.3 | 3 | 0.9
|  | F-G | 0.6 | 2.5 | 1.5 | 0.6 | 2.5 | 1.5 | 0.6 | 2.5 | 1.5 | 0.6 | 2.5 | 1.5 | 0.6 | 2.5 | 1.5 | 0.6 | 2.5 | 1.5 | 0.6 | 2.5 | 1.5 | 0.6 | 2.5 | 1.5
|  | F-H | 0.5 | 3 | 1.5 | 0.5 | 3 | 1.5 | 0.5 | 3 | 1.5 | 0.5 | 3 | 1.5 | 0.5 | 3 | 1.5 | 0.5 | 3 | 1.5 | 0.5 | 3 | 1.5 | 0.5 | 3 | 1.5
|  | H-I | 0.3 | 3 | 0.9 | 0.3 | 3 | 0.9 | 0.3 | 3 | 0.9 | 0.3 | 3 | 0.9 | 0.3 | 3 | 0.9 | 0.3 | 3 | 0.9 | 0.3 | 3 | 0.9 | 0.3 | 3 | 0.9
|  | I-J | 0.2 | 1 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 1 | 0.2
|  | I-K | 0.3 | 2.5 | 0.75 | 0.3 | 2.5 | 0.75 | 0.3 | 2.5 | 0.75 | 0.3 | 2.5 | 0.75 | 0.3 | 2.5 | 0.75 | 0.3 | 2.5 | 0.75 | 0.3 | 2.5 | 0.75 | 0.3 | 2.5 | 0.75
|  | TOTAL | 3.9 | 2.235 | 8.7164 | 3.9 | 2.5769 | 10.05 | 3.9 | 2.5769 | 10.05 | 3.9 | 2.235 | 8.7164 | 3.9 | 2.235 | 8.7164 | 3.9 | 2.235 | 8.7164 | 3.9 | 2.235 | 8.7164 | 3.9 | 2.235 | 8.7164
Case 2 |  |  | LOAD Pt. M1 |  |  | LOAD Pt. M2 |  |  | LOAD Pt. M3 |  |  | LOAD Pt. M4 |  |  | LOAD Pt. M5 |  |  | LOAD Pt. M6 |  |  | LOAD Pt. M7 |  |  | LOAD Pt. M8
| COMPONENT FAILURE |  | ʎ (f/yr) | r (hrs) | U (hours/year) | ʎ (f/yr) | r (hrs) | U (hours/year) | ʎ (f/yr) | r (hrs) | U (hours/year) | ʎ (f/yr) | r (hrs) | U (hours/year) | ʎ (f/yr) | r (hrs) | U (hours/year) | ʎ (f/yr) | r (hrs) | U (hours/year) | ʎ (f/yr) | r (hrs) | U (hours/year) | ʎ (f/yr) | r (hrs) | U (hours/year)
| MAIN | A-B | 0.6 | 2.5 | 1.5 | 0.6 | 2.5 | 1.5 | 0.6 | 2.5 | 1.5 | 0.6 | 2.5 | 1.5 | 0.6 | 2.5 | 1.5 | 0.6 | 2.5 | 1.5 | 0.6 | 2.5 | 1.5 | 0.6 | 2.5 | 1.5
|  | B-C | 0.4 | 0.333 | 0.1332 | 0.4 | 2 | 0.8 | 0.4 | 2 | 0.8 | 0.4 | 0.333 | 0.1332 | 0.4 | 0.333 | 0.1332 | 0.4 | 0.333 | 0.1332 | 0.4 | 0.333 | 0.1332 | 0.4 | 0.333 | 0.1332
|  | C-D | 0.4 | 0.333 | 0.1332 | 0.4 | 0.333 | 0.1332 | 0.4 | 2 | 0.8 | 0.4 | 0.333 | 0.1332 | 0.4 | 0.333 | 0.1332 | 0.4 | 0.333 | 0.1332 | 0.4 | 0.333 | 0.1332 | 0.4 | 0.333 | 0.1332
|  | B-E | 0.3 | 4 | 1.2 | 0.3 | 4 | 1.2 | 0.3 | 4 | 1.2 | 0.3 | 4 | 1.2 | 0.3 | 4 | 1.2 | 0.3 | 4 | 1.2 | 0.3 | 4 | 1.2 | 0.3 | 4 | 1.2
|  | E-F | 0.3 | 3 | 0.9 | 0.3 | 3 | 0.9 | 0.3 | 3 | 0.9 | 0.3 | 3 | 0.9 | 0.3 | 3 | 0.9 | 0.3 | 3 | 0.9 | 0.3 | 3 | 0.9 | 0.3 | 3 | 0.9
|  | F-G | 0.6 | 2.5 | 1.5 | 0.6 | 2.5 | 1.5 | 0.6 | 2.5 | 1.5 | 0.6 | 2.5 | 1.5 | 0.6 | 2.5 | 1.5 | 0.6 | 2.5 | 1.5 | 0.6 | 2.5 | 1.5 | 0.6 | 2.5 | 1.5
|  | F-H | 0.5 | 3 | 1.5 | 0.5 | 3 | 1.5 | 0.5 | 3 | 1.5 | 0.5 | 3 | 1.5 | 0.5 | 3 | 1.5 | 0.5 | 3 | 1.5 | 0.5 | 3 | 1.5 | 0.5 | 3 | 1.5
|  | H-I | 0.3 | 3 | 0.9 | 0.3 | 3 | 0.9 | 0.3 | 3 | 0.9 | 0.3 | 3 | 0.9 | 0.3 | 3 | 0.9 | 0.3 | 3 | 0.9 | 0.3 | 3 | 0.9 | 0.3 | 3 | 0.9
|  | I-J | 0.2 | 1 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 1 | 0.2
|  | I-K | 0.3 | 2.5 | 0.75 | 0.3 | 2.5 | 0.75 | 0.3 | 2.5 | 0.75 | 0.3 | 2.5 | 0.75 | 0.3 | 2.5 | 0.75 | 0.3 | 2.5 | 0.75 | 0.3 | 2.5 | 0.75 | 0.3 | 2.5 | 0.75
|  | TOTAL | 3.9 | 2.235 | 8.7164 | 3.9 | 2.4059 | 9.3832 | 3.9 | 2.5769 | 10.05 | 3.9 | 2.235 | 8.7164 | 3.9 | 2.235 | 8.7164 | 3.9 | 2.235 | 8.7164 | 3.9 | 2.235 | 8.7164 | 3.9 | 2.235 | 8.7164
Case 3 |  |  | LOAD Pt. M1 |  |  | LOAD Pt. M2 |  |  | LOAD Pt. M3 |  |  | LOAD Pt. M4 |  |  | LOAD Pt. M5 |  |  | LOAD Pt. M6 |  |  | LOAD Pt. M7 |  |  | LOAD Pt. M8
| COMPONENT FAILURE |  | ʎ (f/yr) | r (hrs) | U (hours/year) | ʎ (f/yr) | r (hrs) | U (hours/year) | ʎ (f/yr) | r (hrs) | U (hours/year) | ʎ (f/yr) | r (hrs) | U (hours/year) | ʎ (f/yr) | r (hrs) | U (hours/year) | ʎ (f/yr) | r (hrs) | U (hours/year) | ʎ (f/yr) | r (hrs) | U (hours/year) | ʎ (f/yr) | r (hrs) | U (hours/year)
| MAIN | A-B | 0.6 | 2.5 | 1.5 | 0.6 | 2.5 | 1.5 | 0.6 | 2.5 | 1.5 | 0.6 | 2.5 | 1.5 | 0.6 | 2.5 | 1.5 | 0.6 | 2.5 | 1.5 | 0.6 | 2.5 | 1.5 | 0.6 | 2.5 | 1.5
|  | B-C | 0.4 | 0.333 | 0.1332 | 0.4 | 2 | 0.8 | 0.4 | 2 | 0.8 | 0.4 | 0.333 | 0.1332 | 0.4 | 0.333 | 0.1332 | 0.4 | 0.333 | 0.1332 | 0.4 | 0.333 | 0.1332 | 0.4 | 0.333 | 0.1332
|  | C-D | 0.4 | 0.333 | 0.1332 | 0.4 | 0.333 | 0.1332 | 0.4 | 2 | 0.8 | 0.4 | 0.333 | 0.1332 | 0.4 | 0.333 | 0.1332 | 0.4 | 0.333 | 0.1332 | 0.4 | 0.333 | 0.1332 | 0.4 | 0.333 | 0.1332
|  | B-E | 0.3 | 0.333 | 0.0999 | 0.3 | 0.333 | 0.0999 | 0.3 | 0.333 | 0.0999 | 0.3 | 4 | 1.2 | 0.3 | 4 | 1.2 | 0.3 | 4 | 1.2 | 0.3 | 4 | 1.2 | 0.3 | 4 | 1.2
|  | E-F | 0.3 | 0.333 | 0.0999 | 0.3 | 0.333 | 0.0999 | 0.3 | 0.333 | 0.0999 | 0.3 | 3 | 0.9 | 0.3 | 3 | 0.9 | 0.3 | 3 | 0.9 | 0.3 | 3 | 0.9 | 0.3 | 3 | 0.9
|  | F-G | 0.6 | 0.333 | 0.1998 | 0.6 | 0.333 | 0.1998 | 0.6 | 0.333 | 0.1998 | 0.6 | 2.5 | 1.5 | 0.6 | 2.5 | 1.5 | 0.6 | 2.5 | 1.5 | 0.6 | 2.5 | 1.5 | 0.6 | 2.5 | 1.5
|  | F-H | 0.5 | 0.333 | 0.1665 | 0.5 | 0.333 | 0.1665 | 0.5 | 0.333 | 0.1665 | 0.5 | 3 | 1.5 | 0.5 | 3 | 1.5 | 0.5 | 3 | 1.5 | 0.5 | 3 | 1.5 | 0.5 | 3 | 1.5
|  | H-I | 0.3 | 0.333 | 0.0999 | 0.3 | 0.333 | 0.0999 | 0.3 | 0.333 | 0.0999 | 0.3 | 3 | 0.9 | 0.3 | 3 | 0.9 | 0.3 | 3 | 0.9 | 0.3 | 3 | 0.9 | 0.3 | 3 | 0.9
|  | I-J | 0.2 | 0.333 | 0.0666 | 0.2 | 0.333 | 0.0666 | 0.2 | 0.333 | 0.0666 | 0.2 | 1 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 1 | 0.2
|  | I-K | 0.3 | 0.333 | 0.0999 | 0.3 | 0.333 | 0.0999 | 0.3 | 0.333 | 0.0999 | 0.3 | 2.5 | 0.75 | 0.3 | 2.5 | 0.75 | 0.3 | 2.5 | 0.75 | 0.3 | 2.5 | 0.75 | 0.3 | 2.5 | 0.75
|  | TOTAL | 3.9 | 0.66638 | 2.5989 | 3.9 | 0.83736 | 3.2657 | 3.9 | 1.0083 | 3.9325 | 3.9 | 2.235 | 8.7164 | 3.9 | 2.235 | 8.7164 | 3.9 | 2.235 | 8.7164 | 3.9 | 2.235 | 8.7164 | 3.9 | 2.235 | 8.7164
Case 4 |  |  | LOAD Pt. M1 |  |  | LOAD Pt. M2 |  |  | LOAD Pt. M3 |  |  | LOAD Pt. M4 |  |  | LOAD Pt. M5 |  |  | LOAD Pt. M6 |  |  | LOAD Pt. M7 |  |  | LOAD Pt. M8
| COMPONENT FAILURE |  | ʎ (f/yr) | r (hrs) | U (hours/year) | ʎ (f/yr) | r (hrs) | U (hours/year) | ʎ (f/yr) | r (hrs) | U (hours/year) | ʎ (f/yr) | r (hrs) | U (hours/year) | ʎ (f/yr) | r (hrs) | U (hours/year) | ʎ (f/yr) | r (hrs) | U (hours/year) | ʎ (f/yr) | r (hrs) | U (hours/year) | ʎ (f/yr) | r (hrs) | U (hours/year)
| MAIN | A-B | 0.6 | 2.5 | 1.5 | 0.6 | 2.5 | 1.5 | 0.6 | 2.5 | 1.5 | 0.6 | 2.5 | 1.5 | 0.6 | 2.5 | 1.5 | 0.6 | 2.5 | 1.5 | 0.6 | 2.5 | 1.5 | 0.6 | 2.5 | 1.5
|  | B-C | 0.4 | 0.333 | 0.1332 | 0.4 | 2 | 0.8 | 0.4 | 2 | 0.8 | 0.4 | 0.333 | 0.1332 | 0.4 | 0.333 | 0.1332 | 0.4 | 0.333 | 0.1332 | 0.4 | 0.333 | 0.1332 | 0.4 | 0.333 | 0.1332
|  | C-D | 0.4 | 0.333 | 0.1332 | 0.4 | 0.333 | 0.1332 | 0.4 | 2 | 0.8 | 0.4 | 0.333 | 0.1332 | 0.4 | 0.333 | 0.1332 | 0.4 | 0.333 | 0.1332 | 0.4 | 0.333 | 0.1332 | 0.4 | 0.333 | 0.1332
|  | B-E | 0.3 | 0.333 | 0.0999 | 0.3 | 0.333 | 0.0999 | 0.3 | 0.333 | 0.0999 | 0.3 | 4 | 1.2 | 0.3 | 4 | 1.2 | 0.3 | 4 | 1.2 | 0.3 | 4 | 1.2 | 0.3 | 4 | 1.2
|  | E-F | 0.3 | 0.333 | 0.0999 | 0.3 | 0.333 | 0.0999 | 0.3 | 0.333 | 0.0999 | 0.3 | 0.333 | 0.0999 | 0.3 | 3 | 0.9 | 0.3 | 3 | 0.9 | 0.3 | 3 | 0.9 | 0.3 | 3 | 0.9
|  | F-G | 0.6 | 0.333 | 0.1998 | 0.6 | 0.333 | 0.1998 | 0.6 | 0.333 | 0.1998 | 0.6 | 0.333 | 0.1998 | 0.6 | 2.5 | 1.5 | 0.6 | 2.5 | 1.5 | 0.6 | 2.5 | 1.5 | 0.6 | 2.5 | 1.5
|  | F-H | 0.5 | 0.333 | 0.1665 | 0.5 | 0.333 | 0.1665 | 0.5 | 0.333 | 0.1665 | 0.5 | 0.333 | 0.1665 | 0.5 | 3 | 1.5 | 0.5 | 3 | 1.5 | 0.5 | 3 | 1.5 | 0.5 | 3 | 1.5
|  | H-I | 0.3 | 0.333 | 0.0999 | 0.3 | 0.333 | 0.0999 | 0.3 | 0.333 | 0.0999 | 0.3 | 0.333 | 0.0999 | 0.3 | 3 | 0.9 | 0.3 | 3 | 0.9 | 0.3 | 3 | 0.9 | 0.3 | 3 | 0.9
|  | I-J | 0.2 | 0.333 | 0.0666 | 0.2 | 0.333 | 0.0666 | 0.2 | 0.333 | 0.0666 | 0.2 | 0.333 | 0.0666 | 0.2 | 1 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 1 | 0.2
|  | I-K | 0.3 | 0.333 | 0.0999 | 0.3 | 0.333 | 0.0999 | 0.3 | 0.333 | 0.0999 | 0.3 | 0.333 | 0.0999 | 0.3 | 2.5 | 0.75 | 0.3 | 2.5 | 0.75 | 0.3 | 2.5 | 0.75 | 0.3 | 2.5 | 0.75
|  | TOTAL | 3.9 | 0.66638 | 2.5989 | 3.9 | 0.83736 | 3.2657 | 3.9 | 1.0083 | 3.9325 | 3.9 | 0.94846 | 3.699 | 3.9 | 2.235 | 8.7164 | 3.9 | 2.235 | 8.7164 | 3.9 | 2.235 | 8.7164 | 3.9 | 2.235 | 8.7164
Case 5 |  |  | LOAD Pt. M1 |  |  | LOAD Pt. M2 |  |  | LOAD Pt. M3 |  |  | LOAD Pt. M4 |  |  | LOAD Pt. M5 |  |  | LOAD Pt. M6 |  |  | LOAD Pt. M7 |  |  | LOAD Pt. M8
| COMPONENT FAILURE |  | ʎ (f/yr) | r (hrs) | U (hours/year) | ʎ (f/yr) | r (hrs) | U (hours/year) | ʎ (f/yr) | r (hrs) | U (hours/year) | ʎ (f/yr) | r (hrs) | U (hours/year) | ʎ (f/yr) | r (hrs) | U (hours/year) | ʎ (f/yr) | r (hrs) | U (hours/year) | ʎ (f/yr) | r (hrs) | U (hours/year) | ʎ (f/yr) | r (hrs) | U (hours/year)
| MAIN | A-B | 0.6 | 2.5 | 1.5 | 0.6 | 2.5 | 1.5 | 0.6 | 2.5 | 1.5 | 0.6 | 2.5 | 1.5 | 0.6 | 2.5 | 1.5 | 0.6 | 2.5 | 1.5 | 0.6 | 2.5 | 1.5 | 0.6 | 2.5 | 1.5
|  | B-C | 0.4 | 0.333 | 0.1332 | 0.4 | 2 | 0.8 | 0.4 | 2 | 0.8 | 0.4 | 0.333 | 0.1332 | 0.4 | 0.333 | 0.1332 | 0.4 | 0.333 | 0.1332 | 0.4 | 0.333 | 0.1332 | 0.4 | 0.333 | 0.1332
|  | C-D | 0.4 | 0.333 | 0.1332 | 0.4 | 0.333 | 0.1332 | 0.4 | 2 | 0.8 | 0.4 | 0.333 | 0.1332 | 0.4 | 0.333 | 0.1332 | 0.4 | 0.333 | 0.1332 | 0.4 | 0.333 | 0.1332 | 0.4 | 0.333 | 0.1332
|  | B-E | 0.3 | 0.333 | 0.0999 | 0.3 | 0.333 | 0.0999 | 0.3 | 0.333 | 0.0999 | 0.3 | 4 | 1.2 | 0.3 | 4 | 1.2 | 0.3 | 4 | 1.2 | 0.3 | 4 | 1.2 | 0.3 | 4 | 1.2
|  | E-F | 0.3 | 0.333 | 0.0999 | 0.3 | 0.333 | 0.0999 | 0.3 | 0.333 | 0.0999 | 0.3 | 0.333 | 0.0999 | 0.3 | 3 | 0.9 | 0.3 | 3 | 0.9 | 0.3 | 3 | 0.9 | 0.3 | 3 | 0.9
|  | F-G | 0.6 | 0.333 | 0.1998 | 0.6 | 0.333 | 0.1998 | 0.6 | 0.333 | 0.1998 | 0.6 | 0.333 | 0.1998 | 0.6 | 2.5 | 1.5 | 0.6 | 0.333 | 0.1998 | 0.6 | 0.333 | 0.1998 | 0.6 | 0.333 | 0.1998
|  | F-H | 0.5 | 0.333 | 0.1665 | 0.5 | 0.333 | 0.1665 | 0.5 | 0.333 | 0.1665 | 0.5 | 0.333 | 0.1665 | 0.5 | 3 | 1.5 | 0.5 | 3 | 1.5 | 0.5 | 3 | 1.5 | 0.5 | 3 | 1.5
|  | H-I | 0.3 | 0.333 | 0.0999 | 0.3 | 0.333 | 0.0999 | 0.3 | 0.333 | 0.0999 | 0.3 | 0.333 | 0.0999 | 0.3 | 3 | 0.9 | 0.3 | 3 | 0.9 | 0.3 | 3 | 0.9 | 0.3 | 3 | 0.9
|  | I-J | 0.2 | 0.333 | 0.0666 | 0.2 | 0.333 | 0.0666 | 0.2 | 0.333 | 0.0666 | 0.2 | 0.333 | 0.0666 | 0.2 | 1 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 1 | 0.2
|  | I-K | 0.3 | 0.333 | 0.0999 | 0.3 | 0.333 | 0.0999 | 0.3 | 0.333 | 0.0999 | 0.3 | 0.333 | 0.0999 | 0.3 | 2.5 | 0.75 | 0.3 | 2.5 | 0.75 | 0.3 | 2.5 | 0.75 | 0.3 | 2.5 | 0.75
|  | TOTAL | 3.9 | 0.66638 | 2.5989 | 3.9 | 0.83736 | 3.2657 | 3.9 | 1.0083 | 3.9325 | 3.9 | 0.94846 | 3.699 | 3.9 | 2.235 | 8.7164 | 3.9 | 1.9016 | 7.4162 | 3.9 | 1.9016 | 7.4162 | 3.9 | 1.9016 | 7.4162
Case 6 |  |  | LOAD Pt. M1 |  |  | LOAD Pt. M2 |  |  | LOAD Pt. M3 |  |  | LOAD Pt. M4 |  |  | LOAD Pt. M5 |  |  | LOAD Pt. M6 |  |  | LOAD Pt. M7 |  |  | LOAD Pt. M8
| COMPONENT FAILURE |  | ʎ (f/yr) | r (hrs) | U (hours/year) | ʎ (f/yr) | r (hrs) | U (hours/year) | ʎ (f/yr) | r (hrs) | U (hours/year) | ʎ (f/yr) | r (hrs) | U (hours/year) | ʎ (f/yr) | r (hrs) | U (hours/year) | ʎ (f/yr) | r (hrs) | U (hours/year) | ʎ (f/yr) | r (hrs) | U (hours/year) | ʎ (f/yr) | r (hrs) | U (hours/year)
| MAIN | A-B | 0.6 | 2.5 | 1.5 | 0.6 | 2.5 | 1.5 | 0.6 | 2.5 | 1.5 | 0.6 | 2.5 | 1.5 | 0.6 | 2.5 | 1.5 | 0.6 | 2.5 | 1.5 | 0.6 | 2.5 | 1.5 | 0.6 | 2.5 | 1.5
|  | B-C | 0.4 | 0.333 | 0.1332 | 0.4 | 2 | 0.8 | 0.4 | 2 | 0.8 | 0.4 | 0.333 | 0.1332 | 0.4 | 0.333 | 0.1332 | 0.4 | 0.333 | 0.1332 | 0.4 | 0.333 | 0.1332 | 0.4 | 0.333 | 0.1332
|  | C-D | 0.4 | 0.333 | 0.1332 | 0.4 | 0.333 | 0.1332 | 0.4 | 2 | 0.8 | 0.4 | 0.333 | 0.1332 | 0.4 | 0.333 | 0.1332 | 0.4 | 0.333 | 0.1332 | 0.4 | 0.333 | 0.1332 | 0.4 | 0.333 | 0.1332
|  | B-E | 0.3 | 0.333 | 0.0999 | 0.3 | 0.333 | 0.0999 | 0.3 | 0.333 | 0.0999 | 0.3 | 4 | 1.2 | 0.3 | 4 | 1.2 | 0.3 | 4 | 1.2 | 0.3 | 4 | 1.2 | 0.3 | 4 | 1.2
|  | E-F | 0.3 | 0.333 | 0.0999 | 0.3 | 0.333 | 0.0999 | 0.3 | 0.333 | 0.0999 | 0.3 | 0.333 | 0.0999 | 0.3 | 3 | 0.9 | 0.3 | 3 | 0.9 | 0.3 | 3 | 0.9 | 0.3 | 3 | 0.9
|  | F-G | 0.6 | 0.333 | 0.1998 | 0.6 | 0.333 | 0.1998 | 0.6 | 0.333 | 0.1998 | 0.6 | 0.333 | 0.1998 | 0.6 | 2.5 | 1.5 | 0.6 | 0.333 | 0.1998 | 0.6 | 0.333 | 0.1998 | 0.6 | 0.333 | 0.1998
|  | F-H | 0.5 | 0.333 | 0.1665 | 0.5 | 0.333 | 0.1665 | 0.5 | 0.333 | 0.1665 | 0.5 | 0.333 | 0.1665 | 0.5 | 0.333 | 0.1665 | 0.5 | 3 | 1.5 | 0.5 | 3 | 1.5 | 0.5 | 3 | 1.5
|  | H-I | 0.3 | 0.333 | 0.0999 | 0.3 | 0.333 | 0.0999 | 0.3 | 0.333 | 0.0999 | 0.3 | 0.333 | 0.0999 | 0.3 | 0.333 | 0.0999 | 0.3 | 3 | 0.9 | 0.3 | 3 | 0.9 | 0.3 | 3 | 0.9
|  | I-J | 0.2 | 0.333 | 0.0666 | 0.2 | 0.333 | 0.0666 | 0.2 | 0.333 | 0.0666 | 0.2 | 0.333 | 0.0666 | 0.2 | 0.333 | 0.0666 | 0.2 | 1 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 1 | 0.2
|  | I-K | 0.3 | 0.333 | 0.0999 | 0.3 | 0.333 | 0.0999 | 0.3 | 0.333 | 0.0999 | 0.3 | 0.333 | 0.0999 | 0.3 | 0.333 | 0.0999 | 0.3 | 2.5 | 0.75 | 0.3 | 2.5 | 0.75 | 0.3 | 2.5 | 0.75
|  | TOTAL | 3.9 | 0.66638 | 2.5989 | 3.9 | 0.83736 | 3.2657 | 3.9 | 1.0083 | 3.9325 | 3.9 | 0.94846 | 3.699 | 3.9 | 1.487 | 5.7993 | 3.9 | 1.9016 | 7.4162 | 3.9 | 1.9016 | 7.4162 | 3.9 | 1.9016 | 7.4162
Case 7 |  |  | LOAD Pt. M1 |  |  | LOAD Pt. M2 |  |  | LOAD Pt. M3 |  |  | LOAD Pt. M4 |  |  | LOAD Pt. M5 |  |  | LOAD Pt. M6 |  |  | LOAD Pt. M7 |  |  | LOAD Pt. M8
| COMPONENT FAILURE |  | ʎ (f/yr) | r (hrs) | U (hours/year) | ʎ (f/yr) | r (hrs) | U (hours/year) | ʎ (f/yr) | r (hrs) | U (hours/year) | ʎ (f/yr) | r (hrs) | U (hours/year) | ʎ (f/yr) | r (hrs) | U (hours/year) | ʎ (f/yr) | r (hrs) | U (hours/year) | ʎ (f/yr) | r (hrs) | U (hours/year) | ʎ (f/yr) | r (hrs) | U (hours/year)
| MAIN | A-B | 0.6 | 2.5 | 1.5 | 0.6 | 2.5 | 1.5 | 0.6 | 2.5 | 1.5 | 0.6 | 2.5 | 1.5 | 0.6 | 2.5 | 1.5 | 0.6 | 2.5 | 1.5 | 0.6 | 2.5 | 1.5 | 0.6 | 2.5 | 1.5
|  | B-C | 0.4 | 0.333 | 0.1332 | 0.4 | 2 | 0.8 | 0.4 | 2 | 0.8 | 0.4 | 0.333 | 0.1332 | 0.4 | 0.333 | 0.1332 | 0.4 | 0.333 | 0.1332 | 0.4 | 0.333 | 0.1332 | 0.4 | 0.333 | 0.1332
|  | C-D | 0.4 | 0.333 | 0.1332 | 0.4 | 0.333 | 0.1332 | 0.4 | 2 | 0.8 | 0.4 | 0.333 | 0.1332 | 0.4 | 0.333 | 0.1332 | 0.4 | 0.333 | 0.1332 | 0.4 | 0.333 | 0.1332 | 0.4 | 0.333 | 0.1332
|  | B-E | 0.3 | 0.333 | 0.0999 | 0.3 | 0.333 | 0.0999 | 0.3 | 0.333 | 0.0999 | 0.3 | 4 | 1.2 | 0.3 | 4 | 1.2 | 0.3 | 4 | 1.2 | 0.3 | 4 | 1.2 | 0.3 | 4 | 1.2
|  | E-F | 0.3 | 0.333 | 0.0999 | 0.3 | 0.333 | 0.0999 | 0.3 | 0.333 | 0.0999 | 0.3 | 0.333 | 0.0999 | 0.3 | 3 | 0.9 | 0.3 | 3 | 0.9 | 0.3 | 3 | 0.9 | 0.3 | 3 | 0.9
|  | F-G | 0.6 | 0.333 | 0.1998 | 0.6 | 0.333 | 0.1998 | 0.6 | 0.333 | 0.1998 | 0.6 | 0.333 | 0.1998 | 0.6 | 2.5 | 1.5 | 0.6 | 0.333 | 0.1998 | 0.6 | 0.333 | 0.1998 | 0.6 | 0.333 | 0.1998
|  | F-H | 0.5 | 0.333 | 0.1665 | 0.5 | 0.333 | 0.1665 | 0.5 | 0.333 | 0.1665 | 0.5 | 0.333 | 0.1665 | 0.5 | 0.333 | 0.1665 | 0.5 | 3 | 1.5 | 0.5 | 3 | 1.5 | 0.5 | 3 | 1.5
|  | H-I | 0.3 | 0.333 | 0.0999 | 0.3 | 0.333 | 0.0999 | 0.3 | 0.333 | 0.0999 | 0.3 | 0.333 | 0.0999 | 0.3 | 0.333 | 0.0999 | 0.3 | 3 | 0.9 | 0.3 | 3 | 0.9 | 0.3 | 3 | 0.9
|  | I-J | 0.2 | 0.333 | 0.0666 | 0.2 | 0.333 | 0.0666 | 0.2 | 0.333 | 0.0666 | 0.2 | 0.333 | 0.0666 | 0.2 | 0.333 | 0.0666 | 0.2 | 0.333 | 0.0666 | 0.2 | 1 | 0.2 | 0.2 | 1 | 0.2
|  | I-K | 0.3 | 0.333 | 0.0999 | 0.3 | 0.333 | 0.0999 | 0.3 | 0.333 | 0.0999 | 0.3 | 0.333 | 0.0999 | 0.3 | 0.333 | 0.0999 | 0.3 | 0.333 | 0.0999 | 0.3 | 2.5 | 0.75 | 0.3 | 2.5 | 0.75
|  | TOTAL | 3.9 | 0.66638 | 2.5989 | 3.9 | 0.83736 | 3.2657 | 3.9 | 1.0083 | 3.9325 | 3.9 | 0.94846 | 3.699 | 3.9 | 1.487 | 5.7993 | 3.9 | 1.7007 | 6.6327 | 3.9 | 1.9016 | 7.4162 | 3.9 | 1.9016 | 7.4162
Case 8 |  |  | LOAD Pt. M1 |  |  | LOAD Pt. M2 |  |  | LOAD Pt. M3 |  |  | LOAD Pt. M4 |  |  | LOAD Pt. M5 |  |  | LOAD Pt. M6 |  |  | LOAD Pt. M7 |  |  | LOAD Pt. M8
| COMPONENT FAILURE |  | ʎ (f/yr) | r (hrs) | U (hours/year) | ʎ (f/yr) | r (hrs) | U (hours/year) | ʎ (f/yr) | r (hrs) | U (hours/year) | ʎ (f/yr) | r (hrs) | U (hours/year) | ʎ (f/yr) | r (hrs) | U (hours/year) | ʎ (f/yr) | r (hrs) | U (hours/year) | ʎ (f/yr) | r (hrs) | U (hours/year) | ʎ (f/yr) | r (hrs) | U (hours/year)
| MAIN | A-B | 0.6 | 2.5 | 1.5 | 0.6 | 2.5 | 1.5 | 0.6 | 2.5 | 1.5 | 0.6 | 2.5 | 1.5 | 0.6 | 2.5 | 1.5 | 0.6 | 2.5 | 1.5 | 0.6 | 2.5 | 1.5 | 0.6 | 2.5 | 1.5
|  | B-C | 0.4 | 0.333 | 0.1332 | 0.4 | 2 | 0.8 | 0.4 | 2 | 0.8 | 0.4 | 0.333 | 0.1332 | 0.4 | 0.333 | 0.1332 | 0.4 | 0.333 | 0.1332 | 0.4 | 0.333 | 0.1332 | 0.4 | 0.333 | 0.1332
|  | C-D | 0.4 | 0.333 | 0.1332 | 0.4 | 0.333 | 0.1332 | 0.4 | 2 | 0.8 | 0.4 | 0.333 | 0.1332 | 0.4 | 0.333 | 0.1332 | 0.4 | 0.333 | 0.1332 | 0.4 | 0.333 | 0.1332 | 0.4 | 0.333 | 0.1332
|  | B-E | 0.3 | 0.333 | 0.0999 | 0.3 | 0.333 | 0.0999 | 0.3 | 0.333 | 0.0999 | 0.3 | 4 | 1.2 | 0.3 | 4 | 1.2 | 0.3 | 4 | 1.2 | 0.3 | 4 | 1.2 | 0.3 | 4 | 1.2
|  | E-F | 0.3 | 0.333 | 0.0999 | 0.3 | 0.333 | 0.0999 | 0.3 | 0.333 | 0.0999 | 0.3 | 0.333 | 0.0999 | 0.3 | 3 | 0.9 | 0.3 | 3 | 0.9 | 0.3 | 3 | 0.9 | 0.3 | 3 | 0.9
|  | F-G | 0.6 | 0.333 | 0.1998 | 0.6 | 0.333 | 0.1998 | 0.6 | 0.333 | 0.1998 | 0.6 | 0.333 | 0.1998 | 0.6 | 2.5 | 1.5 | 0.6 | 0.333 | 0.1998 | 0.6 | 0.333 | 0.1998 | 0.6 | 0.333 | 0.1998
|  | F-H | 0.5 | 0.333 | 0.1665 | 0.5 | 0.333 | 0.1665 | 0.5 | 0.333 | 0.1665 | 0.5 | 0.333 | 0.1665 | 0.5 | 0.333 | 0.1665 | 0.5 | 3 | 1.5 | 0.5 | 3 | 1.5 | 0.5 | 3 | 1.5
|  | H-I | 0.3 | 0.333 | 0.0999 | 0.3 | 0.333 | 0.0999 | 0.3 | 0.333 | 0.0999 | 0.3 | 0.333 | 0.0999 | 0.3 | 0.333 | 0.0999 | 0.3 | 0.333 | 0.0999 | 0.3 | 3 | 0.9 | 0.3 | 3 | 0.9
|  | I-J | 0.2 | 0.333 | 0.0666 | 0.2 | 0.333 | 0.0666 | 0.2 | 0.333 | 0.0666 | 0.2 | 0.333 | 0.0666 | 0.2 | 0.333 | 0.0666 | 0.2 | 0.333 | 0.0666 | 0.2 | 1 | 0.2 | 0.2 | 1 | 0.2
|  | I-K | 0.3 | 0.333 | 0.0999 | 0.3 | 0.333 | 0.0999 | 0.3 | 0.333 | 0.0999 | 0.3 | 0.333 | 0.0999 | 0.3 | 0.333 | 0.0999 | 0.3 | 0.333 | 0.0999 | 0.3 | 0.333 | 0.0999 | 0.3 | 2.5 | 0.75
|  | TOTAL | 3.9 | 0.66638 | 2.5989 | 3.9 | 0.83736 | 3.2657 | 3.9 | 1.0083 | 3.9325 | 3.9 | 0.94846 | 3.699 | 3.9 | 1.487 | 5.7993 | 3.9 | 1.4955 | 5.8326 | 3.9 | 1.7349 | 6.7661 | 3.9 | 1.9016 | 7.4162

## RESULTS
Case | SAIFI (int/customer-yr) | SAIDI (hours/customer-yr) | CAIDI (hours/customer-interruption) | ASUI | ASAI | ASCI (kWh/customer-yr) | ENS (kWh) | kWh saved | Number of Switches | kWh per Switch
Base Case | 3.9 | 10.05 | 2.5769 | 0.0011473 | 0.99885 | 5.0674 | 520996.02 | 0 | 0 | 0
Case 01 | 3.9 | 8.8189 | 2.2612 | 0.0010067 | 0.99899 | 4.4619 | 458744.6656 | 62251.3544 | 1 | 62251.3544
Case 02 | 3.9 | 8.8189 | 2.2612 | 0.0010067 | 0.99899 | 4.4452 | 457020.7475 | 63975.2725 | 2 | 31987.6362
Case 03 | 3.9 | 6.2749 | 1.6089 | 0.00071631 | 0.99928 | 3.0024 | 308689.4191 | 212306.6009 | 3 | 70768.867
Case 04 | 3.9 | 5.8481 | 1.4995 | 0.00066759 | 0.99933 | 2.5391 | 261050.9622 | 259945.0578 | 4 | 64986.2644
Case 05 | 3.9 | 5.3401 | 1.3692 | 0.0006096 | 0.99939 | 2.3575 | 242383.4967 | 278612.5233 | 5 | 55722.5047
Case 06 | 3.9 | 5.024 | 1.2882 | 0.00057351 | 0.99943 | 2.2514 | 231469.6922 | 289526.3278 | 6 | 48254.388
Case 07 | 3.9 | 4.9689 | 1.2741 | 0.00056723 | 0.99943 | 2.2301 | 229279.034 | 291716.986 | 7 | 41673.8551
Case 08 | #REF! | 4.7044 | #REF! | 0.00053703 | 0.99946 | 2.146 | 220638.0743 | 300357.9457 | 8 | 37544.7432
BASE CASE | U (hours/year) |  | CASE 1 | U (hours/year) |  | CASE 2 | U (hours/year) |  | CASE 3 | U (hours/year) | CASE 4 | U (hours/year) | CASE 5 | U (hours/year) | CASE 6 | U (hours/year) | CASE 7 | U (hours/year) | CASE 8 | U (hours/year)
M1 | 10.05 |  | M1 | 8.7164 |  | M1 | 8.7164 |  | M1 | 2.5989 | M1 | 2.5989 | M1 | 2.5989 | M1 | 2.5989 | M1 | 2.5989 | M1 | 2.5989
M2 | 10.05 |  | M2 | 10.05 |  | M2 | 9.3832 |  | M2 | 3.2657 | M2 | 3.2657 | M2 | 3.2657 | M2 | 3.2657 | M2 | 3.2657 | M2 | 3.2657
M3 | 10.05 |  | M3 | 10.05 |  | M3 | 10.05 |  | M3 | 3.9325 | M3 | 3.9325 | M3 | 3.9325 | M3 | 3.9325 | M3 | 3.9325 | M3 | 3.9325
M4 | 10.05 |  | M4 | 8.7164 |  | M4 | 8.7164 |  | M4 | 8.7164 | M4 | 3.699 | M4 | 3.699 | M4 | 3.699 | M4 | 3.699 | M4 | 3.699
M5 | 10.05 |  | M5 | 8.7164 |  | M5 | 8.7164 |  | M5 | 8.7164 | M5 | 8.7164 | M5 | 8.7164 | M5 | 5.7993 | M5 | 5.7993 | M5 | 5.7993
M6 | 10.05 |  | M6 | 8.7164 |  | M6 | 8.7164 |  | M6 | 8.7164 | M6 | 8.7164 | M6 | 7.4162 | M6 | 7.4162 | M6 | 6.6327 | M6 | 5.8326
M7 | 10.05 |  | M7 | 8.7164 |  | M7 | 8.7164 |  | M7 | 8.7164 | M7 | 8.7164 | M7 | 7.4162 | M7 | 7.4162 | M7 | 7.4162 | M7 | 6.7661
M8 | 10.05 |  | M8 | 8.7164 |  | M8 | 8.7164 |  | M8 | 8.7164 | M8 | 8.7164 | M8 | 7.4162 | M8 | 7.4162 | M8 | 7.4162 | M8 | 7.4162