## DASHBOARD
POWERPLANT AND DISTRIBUTION DESIGN
POWERPLANT SIZE:
27093.30kVA
SUBSTATION SIZE:
13960.14kVA
LOAD TYPES:
RESIDENTIAL
COMMERCIAL
INDUSTRIAL
COMMERCIAL BULK
INDUSTRIAL BULK
This chart isn't available in your version of Excel. Editing this shape or saving this workbook into a different file format will permanently break the chart.

## STUDY AREA 1
STUDY AREA 1, BLOCK 1
[16 empty] | Power Factor | kVA | TRANSFORMER SIZE
LOAD | NO. OF ESTABLISHMENTS | ESTIMATED AVERAGE AMPACITY | NUMBER OF PHASE | VOLTAGE | POWER (kW) | SIMULTANEOUS MAXIMUM DEMAND | = | 448.5(0.6) | + | 179.4(0.7) | + | 0(0.65) | = | 220.5637 | kW | 0.9 | 245.0708 | USE 1 - 300 kVA TRANSFORMER | 300
Residential Load | 130 | 15 | 1 | 230 | 448.5 |  |  | 2 |  | 1.46 |  | 0.86 | [7 empty] | LOAD
Commercial Load | 12 | 65 | 1 | 230 | 179.4 | [14 empty] | Residential Load | 9142.5
Industrial Load | 0 | 0 | 0 | 0 | 0 | [14 empty] | Commercial Load | 6814.9
[20 empty] | Industrial Load | 0
STUDY AREA 1, BLOCK 2
[16 empty] | Power Factor | kVA
LOAD | NO. OF ESTABLISHMENTS | ESTIMATED AVERAGE AMPACITY | NUMBER OF PHASE | VOLTAGE | POWER (kW) | SIMULTANEOUS MAXIMUM DEMAND | = | 552(0.6) | + | 299(0.7) | + | 0(0.65) | = | 308.9562 | kW | 0.9 | 343.2846 | USE 1 - 450 kVA TRANSFORMER | 450
Residential Load | 120 | 20 | 1 | 230 | 552 |  |  | 2 |  | 1.46 |  | 0.86
Commercial Load | 20 | 65 | 1 | 230 | 299
Industrial Load | 0 | 0 | 0 | 0 | 0 | SIMULTANEOUS MAXIMUM DEMAND (BULK) | =
STUDY AREA 1, BLOCK 3
[16 empty] | Power Factor | kVA
LOAD | NO. OF ESTABLISHMENTS | ESTIMATED AVERAGE AMPACITY | NUMBER OF PHASE | VOLTAGE | POWER (kW) | SIMULTANEOUS MAXIMUM DEMAND | = | 1472(0.6) | + | 690(0.7) | + | 0(0.65) | = | 772.4219 | kW | 0.9 | 858.2466 | USE 1 - 1000 kVA TRANSFORMER | 1000
Residential Load | 160 | 40 | 1 | 230 | 1472 |  |  | 2 |  | 1.46 |  | 0.86
Commercial Load | 40 | 75 | 1 | 230 | 690
Commercial Load (Bulk) | 1 | 3000 | 3 | 400 | 2078.461 | SIMULTANEOUS MAXIMUM DEMAND (BULK) | = | 2078(0.7) | [5 empty] | 1616.5808 | kVA |  |  | USE 1 - 2000 kVA TRANSFORMER | 2000
Industrial Load | 0 | 0 | 0 | 0 | 0 |  |  | 0.9
STUDY AREA 1, BLOCK 4
[16 empty] | Power Factor | kVA
LOAD | NO. OF ESTABLISHMENTS | ESTIMATED AVERAGE AMPACITY | NUMBER OF PHASE | VOLTAGE | POWER (kW) | SIMULTANEOUS MAXIMUM DEMAND | = | 276(0.6) | + | 241.5(0.7) | + | 0(0.65) | = | 198.5877 | kW | 0.9 | 220.653 | USE 1 - 225 kVA TRANSFORMER | 225
Residential Load | 80 | 15 | 1 | 230 | 276 |  |  | 2 |  | 1.46 |  | 0.86
Commercial Load | 15 | 70 | 1 | 230 | 241.5
Industrial Load | 0 | 0 | 0 | 0 | 0 | SIMULTANEOUS MAXIMUM DEMAND (BULK) | =
STUDY AREA 1, BLOCK 5
[16 empty] | Power Factor | kVA
LOAD | NO. OF ESTABLISHMENTS | ESTIMATED AVERAGE AMPACITY | NUMBER OF PHASE | VOLTAGE | POWER (kW) | SIMULTANEOUS MAXIMUM DEMAND | = | 276(0.6) | + | 276(0.7) | + | 0(0.65) | = | 215.1288 | kW | 0.9 | 239.032 | USE 1 - 300 kVA TRANSFORMER | 300
Residential Load | 60 | 20 | 1 | 230 | 276 |  |  | 2 |  | 1.46 |  | 0.86
Commercial Load | 15 | 80 | 1 | 230 | 276
Industrial Load | 0 | 0 | 0 | 0 | 0 | SIMULTANEOUS MAXIMUM DEMAND (BULK) | =
STUDY AREA 1, BLOCK 6
[16 empty] | Power Factor | kVA
LOAD | NO. OF ESTABLISHMENTS | ESTIMATED AVERAGE AMPACITY | NUMBER OF PHASE | VOLTAGE | POWER (kW) | SIMULTANEOUS MAXIMUM DEMAND | = | 276(0.6) | + | 414(0.7) | + | 0(0.65) | = | 281.2932 | kW | 0.9 | 312.5479 | USE 1 - 450 kVA TRANSFORMER | 450
Residential Load | 40 | 30 | 1 | 230 | 276 |  |  | 2 |  | 1.46 |  | 0.86
Commercial Load | 20 | 90 | 1 | 230 | 414
Industrial Load | 0 | 0 | 0 | 0 | 0 | SIMULTANEOUS MAXIMUM DEMAND (BULK) | =
STUDY AREA 1, BLOCK 7
[16 empty] | Power Factor | kVA
LOAD | NO. OF ESTABLISHMENTS | ESTIMATED AVERAGE AMPACITY | NUMBER OF PHASE | VOLTAGE | POWER (kW) | SIMULTANEOUS MAXIMUM DEMAND | = | 575(0.6) | + | 402.5(0.7) | + | 0(0.65) | = | 365.4795 | kW | 0.9 | 406.0883 | USE 1 - 450 kVA TRANSFORMER | 450
Residential Load | 100 | 25 | 1 | 230 | 575 |  |  | 2 |  | 1.46 |  | 0.86
Commercial Load | 25 | 70 | 1 | 230 | 402.5
Industrial Load | 0 | 0 | 0 | 0 | 0 | SIMULTANEOUS MAXIMUM DEMAND (BULK) | =
STUDY AREA 1, BLOCK 8
[16 empty] | Power Factor | kVA
LOAD | NO. OF ESTABLISHMENTS | ESTIMATED AVERAGE AMPACITY | NUMBER OF PHASE | VOLTAGE | POWER (kW) | SIMULTANEOUS MAXIMUM DEMAND | = | 517.5(0.6) | + | 1092.5(0.7) | + | 0(0.65) | = | 679.0514 | kW | 0.9 | 754.5015 | USE 1 - 800 kVA TRANSFORMER | 800
Residential Load | 50 | 45 | 1 | 230 | 517.5 |  |  | 2 |  | 1.46 |  | 0.86
Commercial Load | 50 | 95 | 1 | 230 | 1092.5
Commercial Load (Bulk) | 1 | 2900 | 3 | 400 | 2009.1789 | SIMULTANEOUS MAXIMUM DEMAND (BULK) | = | 2009(0.7) | [5 empty] | 1562.6947 | kVA |  |  | USE 1 - 1600 kVA TRANSFORMER | 1600
Industrial Load | 0 | 0 | 0 | 0 | 0 |  |  | 0.9
STUDY AREA 1, BLOCK 9
[16 empty] | Power Factor | kVA
LOAD | NO. OF ESTABLISHMENTS | ESTIMATED AVERAGE AMPACITY | NUMBER OF PHASE | VOLTAGE | POWER (kW) | SIMULTANEOUS MAXIMUM DEMAND | = | 276(0.6) | + | 310.5(0.7) | + | 0(0.65) | = | 231.6699 | kW | 0.9 | 257.411 | USE 1 - 300 kVA TRANSFORMER | 300
Residential Load | 60 | 20 | 1 | 230 | 276 |  |  | 2 |  | 1.46 |  | 0.86
Commercial Load | 15 | 90 | 1 | 230 | 310.5
Industrial Load | 0 | 0 | 0 | 0 | 0 | SIMULTANEOUS MAXIMUM DEMAND (BULK) | =
STUDY AREA 1, BLOCK 10
[16 empty] | Power Factor | kVA
LOAD | NO. OF ESTABLISHMENTS | ESTIMATED AVERAGE AMPACITY | NUMBER OF PHASE | VOLTAGE | POWER (kW) | SIMULTANEOUS MAXIMUM DEMAND | = | 241.5(0.6) | + | 149.5(0.7) | + | 0(0.65) | = | 144.1281 | kW | 0.9 | 160.1423 | USE 1 - 225 kVA TRANSFORMER | 225
Residential Load | 70 | 15 | 1 | 230 | 241.5 |  |  | 2 |  | 1.46 |  | 0.86
Commercial Load | 10 | 65 | 1 | 230 | 149.5
Industrial Load | 0 | 0 | 0 | 0 | 0 | SIMULTANEOUS MAXIMUM DEMAND (BULK) | =
STUDY AREA 1, BLOCK 11
[16 empty] | Power Factor | kVA
LOAD | NO. OF ESTABLISHMENTS | ESTIMATED AVERAGE AMPACITY | NUMBER OF PHASE | VOLTAGE | POWER (kW) | SIMULTANEOUS MAXIMUM DEMAND | = | 414(0.6) | + | 322(0.7) | + | 0(0.65) | = | 278.5836 | kW | 0.9 | 309.5373 | USE 1 - 450 kVA TRANSFORMER | 450
Residential Load | 90 | 20 | 1 | 230 | 414 |  |  | 2 |  | 1.46 |  | 0.86
Commercial Load | 20 | 70 | 1 | 230 | 322
Industrial Load | 0 | 0 | 0 | 0 | 0 | SIMULTANEOUS MAXIMUM DEMAND (BULK) | =
STUDY AREA 1, BLOCK 12
[16 empty] | Power Factor | kVA
LOAD | NO. OF ESTABLISHMENTS | ESTIMATED AVERAGE AMPACITY | NUMBER OF PHASE | VOLTAGE | POWER (kW) | SIMULTANEOUS MAXIMUM DEMAND | = | 552(0.6) | + | 517.5(0.7) | + | 0(0.65) | = | 413.7164 | kW | 0.9 | 459.6849 | USE 1 - 500 kVA TRANSFORMER | 500
Residential Load | 60 | 40 | 1 | 230 | 552 |  |  | 2 |  | 1.46 |  | 0.86
Commercial Load | 25 | 90 | 1 | 230 | 517.5
Industrial Load | 0 | 0 | 0 | 0 | 0 | SIMULTANEOUS MAXIMUM DEMAND (BULK) | =
STUDY AREA 1, BLOCK 13
[16 empty] | Power Factor | kVA
LOAD | NO. OF ESTABLISHMENTS | ESTIMATED AVERAGE AMPACITY | NUMBER OF PHASE | VOLTAGE | POWER (kW) | SIMULTANEOUS MAXIMUM DEMAND | = | 172.5(0.6) | + | 149.5(0.7) | + | 0(0.65) | = | 123.4281 | kW | 0.9 | 137.1423 | USE 1 - 150 kVA TRANSFORMER | 150
Residential Load | 50 | 15 | 1 | 230 | 172.5 |  |  | 2 |  | 1.46 |  | 0.86
Commercial Load | 10 | 65 | 1 | 230 | 149.5
Industrial Load | 0 | 0 | 0 | 0 | 0 | SIMULTANEOUS MAXIMUM DEMAND (BULK) | =
STUDY AREA 1, BLOCK 14
[16 empty] | Power Factor | kVA
LOAD | NO. OF ESTABLISHMENTS | ESTIMATED AVERAGE AMPACITY | NUMBER OF PHASE | VOLTAGE | POWER (kW) | SIMULTANEOUS MAXIMUM DEMAND | = | 368(0.6) | + | 241.5(0.7) | + | 0(0.65) | = | 226.1877 | kW | 0.9 | 251.3196 | USE 1 - 300 kVA TRANSFORMER | 300
Residential Load | 80 | 20 | 1 | 230 | 368 |  |  | 2 |  | 1.46 |  | 0.86
Commercial Load | 15 | 70 | 1 | 230 | 241.5
Industrial Load | 0 | 0 | 0 | 0 | 0 | SIMULTANEOUS MAXIMUM DEMAND (BULK) | =
STUDY AREA 1, BLOCK 15
[16 empty] | Power Factor | kVA
LOAD | NO. OF ESTABLISHMENTS | ESTIMATED AVERAGE AMPACITY | NUMBER OF PHASE | VOLTAGE | POWER (kW) | SIMULTANEOUS MAXIMUM DEMAND | = | 920(0.6) | + | 517.5(0.7) | + | 0(0.65) | = | 524.1164 | kW | 0.9 | 582.3516 | USE 1 - 600 kVA TRANSFORMER | 600
Residential Load | 100 | 40 | 1 | 230 | 920 |  |  | 2 |  | 1.46 |  | 0.86
Commercial Load | 25 | 90 | 1 | 230 | 517.5
Industrial Load | 0 | 0 | 0 | 0 | 0 | SIMULTANEOUS MAXIMUM DEMAND (BULK) | =
STUDY AREA 1, BLOCK 16
[16 empty] | Power Factor | kVA
LOAD | NO. OF ESTABLISHMENTS | ESTIMATED AVERAGE AMPACITY | NUMBER OF PHASE | VOLTAGE | POWER (kW) | SIMULTANEOUS MAXIMUM DEMAND | = | 241.5(0.6) | + | 149.5(0.7) | + | 0(0.65) | = | 144.1281 | kW | 0.9 | 160.1423 | USE 1 - 225 kVA TRANSFORMER | 225
Residential Load | 70 | 15 | 1 | 230 | 241.5 |  |  | 2 |  | 1.46 |  | 0.86
Commercial Load | 10 | 65 | 1 | 230 | 149.5
Industrial Load | 0 | 0 | 0 | 0 | 0 | SIMULTANEOUS MAXIMUM DEMAND (BULK) | =
STUDY AREA 1, BLOCK 17
[16 empty] | Power Factor | kVA
LOAD | NO. OF ESTABLISHMENTS | ESTIMATED AVERAGE AMPACITY | NUMBER OF PHASE | VOLTAGE | POWER (kW) | SIMULTANEOUS MAXIMUM DEMAND | = | 460(0.6) | + | 241.5(0.7) | + | 0(0.65) | = | 253.7877 | kW | 0.9 | 281.9863 | USE 1 - 300 kVA TRANSFORMER | 300
Residential Load | 100 | 20 | 1 | 230 | 460 |  |  | 2 |  | 1.46 |  | 0.86
Commercial Load | 15 | 70 | 1 | 230 | 241.5
Industrial Load | 0 | 0 | 0 | 0 | 0 | SIMULTANEOUS MAXIMUM DEMAND (BULK) | =
STUDY AREA 1, BLOCK 18
[16 empty] | Power Factor | kVA
LOAD | NO. OF ESTABLISHMENTS | ESTIMATED AVERAGE AMPACITY | NUMBER OF PHASE | VOLTAGE | POWER (kW) | SIMULTANEOUS MAXIMUM DEMAND | = | 1104(0.6) | + | 621(0.7) | + | 0(0.65) | = | 628.9397 | kW | 0.9 | 698.8219 | USE 1 - 800 kVA TRANSFORMER | 800
Residential Load | 120 | 40 | 1 | 230 | 1104 |  |  | 2 |  | 1.46 |  | 0.86
Commercial Load | 30 | 90 | 1 | 230 | 621
Industrial Load | 0 | 0 | 0 | 0 | 0 | SIMULTANEOUS MAXIMUM DEMAND (BULK) | =

## STUDY AREA 2
STUDY AREA 2, BLOCK 1
[16 empty] | Power Factor | kVA | TRANSFORMER SIZE
LOAD | NO. OF ESTABLISHMENTS | ESTIMATED AVERAGE AMPACITY | NUMBER OF PHASE | VOLTAGE | POWER (kW) | SIMULTANEOUS MAXIMUM DEMAND | = | 1242(0.6) | + | 414(0.7) | + | 0(0.65) | = | 571.0932 | kW | 0.9 | 634.5479 | USE 1 - 800 kVA TRANSFORMER | 800
Residential Load | 120 | 45 | 1 | 230 | 1242 |  |  | 2 |  | 1.46 |  | 0.86 | [7 empty] | LOAD
Commercial Load | 20 | 90 | 1 | 230 | 414 | [14 empty] | Residential Load | 10683.5
Industrial Load | 0 | 0 | 0 | 0 | 0 | SIMULTANEOUS MAXIMUM DEMAND (BULK) | = | [12 empty] | Commercial Load | 3869.75
[20 empty] | Industrial Load | 0
STUDY AREA 2, BLOCK 2
[16 empty] | Power Factor | kVA
LOAD | NO. OF ESTABLISHMENTS | ESTIMATED AVERAGE AMPACITY | NUMBER OF PHASE | VOLTAGE | POWER (kW) | SIMULTANEOUS MAXIMUM DEMAND | = | 862.5(0.6) | + | 258.75(0.7) | + | 0(0.65) | = | 382.8082 | kW | 0.9 | 425.3425 | USE 1 - 450 kVA TRANSFORMER | 450
Residential Load | 150 | 25 | 1 | 230 | 862.5 |  |  | 2 |  | 1.46 |  | 0.86
Commercial Load | 15 | 75 | 1 | 230 | 258.75
Industrial Load | 0 | 0 | 0 | 0 | 0 | SIMULTANEOUS MAXIMUM DEMAND (BULK) | =
STUDY AREA 2, BLOCK 3
[16 empty] | Power Factor | kVA
LOAD | NO. OF ESTABLISHMENTS | ESTIMATED AVERAGE AMPACITY | NUMBER OF PHASE | VOLTAGE | POWER (kW) | SIMULTANEOUS MAXIMUM DEMAND | = | 172.5(0.6) | + | 74.75(0.7) | + | 0(0.65) | = | 87.589 | kW | 0.9 | 97.3212 | USE 1 - 112.5 kVA TRANSFORMER | 112.5
Residential Load | 50 | 15 | 1 | 230 | 172.5 |  |  | 2 |  | 1.46 |  | 0.86
Commercial Load | 5 | 65 | 1 | 230 | 74.75
Industrial Load (Bulk) | 1 | 1500 | 3 | 1000 | 2598.0762 | SIMULTANEOUS MAXIMUM DEMAND (BULK) | = | 2598(0.7) | [5 empty] | 2020.7259 | kVA |  |  | USE 1 - 2500 kVA TRANSFORMER | 2500
0.9
STUDY AREA 2, BLOCK 4
[16 empty] | Power Factor | kVA
LOAD | NO. OF ESTABLISHMENTS | ESTIMATED AVERAGE AMPACITY | NUMBER OF PHASE | VOLTAGE | POWER (kW) | SIMULTANEOUS MAXIMUM DEMAND | = | 230(0.6) | + | 74.75(0.7) | + | 0(0.65) | = | 104.839 | kW | 0.9 | 116.4878 | USE 1 - 150 kVA TRANSFORMER | 150
Residential Load | 50 | 20 | 1 | 230 | 230 |  |  | 2 |  | 1.46 |  | 0.86
Commercial Load | 5 | 65 | 1 | 230 | 74.75
Industrial Load | 0 | 0 | 0 | 0 | 0 | SIMULTANEOUS MAXIMUM DEMAND (BULK) | =
STUDY AREA 2, BLOCK 5
[16 empty] | Power Factor | kVA
LOAD | NO. OF ESTABLISHMENTS | ESTIMATED AVERAGE AMPACITY | NUMBER OF PHASE | VOLTAGE | POWER (kW) | SIMULTANEOUS MAXIMUM DEMAND | = | 172.5(0.6) | + | 74.75(0.7) | + | 0(0.65) | = | 87.589 | kW | 0.9 | 97.3212 | USE 1 - 112.5 kVA TRANSFORMER | 112.5
Residential Load | 50 | 15 | 1 | 230 | 172.5 |  |  | 2 |  | 1.46 |  | 0.86
Commercial Load | 5 | 65 | 1 | 230 | 74.75
Industrial Load | 0 | 0 | 0 | 0 | 0 | SIMULTANEOUS MAXIMUM DEMAND (BULK) | =
STUDY AREA 2, BLOCK 6
[16 empty] | Power Factor | kVA
LOAD | NO. OF ESTABLISHMENTS | ESTIMATED AVERAGE AMPACITY | NUMBER OF PHASE | VOLTAGE | POWER (kW) | SIMULTANEOUS MAXIMUM DEMAND | = | 920(0.6) | + | 546.25(0.7) | + | 0(0.65) | = | 537.9007 | kW | 0.9 | 597.6674 | USE 1 - 600 kVA TRANSFORMER | 600
Residential Load | 100 | 40 | 1 | 230 | 920 |  |  | 2 |  | 1.46 |  | 0.86
Commercial Load | 25 | 95 | 1 | 230 | 546.25
Industrial Load | 0 | 0 | 0 | 0 | 0 | SIMULTANEOUS MAXIMUM DEMAND (BULK) | =
STUDY AREA 2, BLOCK 7
[16 empty] | Power Factor | kVA
LOAD | NO. OF ESTABLISHMENTS | ESTIMATED AVERAGE AMPACITY | NUMBER OF PHASE | VOLTAGE | POWER (kW) | SIMULTANEOUS MAXIMUM DEMAND | = | 920(0.6) | + | 276(0.7) | + | 0(0.65) | = | 408.3288 | kW | 0.9 | 453.6986 | USE 1 - 500 kVA TRANSFORMER | 500
Residential Load | 160 | 25 | 1 | 230 | 920 |  |  | 2 |  | 1.46 |  | 0.86
Commercial Load | 15 | 80 | 1 | 230 | 276
Industrial Load | 0 | 0 | 0 | 0 | 0 | SIMULTANEOUS MAXIMUM DEMAND (BULK) | =
STUDY AREA 2, BLOCK 8
[16 empty] | Power Factor | kVA
LOAD | NO. OF ESTABLISHMENTS | ESTIMATED AVERAGE AMPACITY | NUMBER OF PHASE | VOLTAGE | POWER (kW) | SIMULTANEOUS MAXIMUM DEMAND | = | 598(0.6) | + | 149.5(0.7) | + | 0(0.65) | = | 251.0781 | kW | 0.9 | 278.9756 | USE 1 - 300 kVA TRANSFORMER | 300
Residential Load | 130 | 20 | 1 | 230 | 598 |  |  | 2 |  | 1.46 |  | 0.86
Commercial Load | 10 | 65 | 1 | 230 | 149.5
Industrial Load | 0 | 0 | 0 | 0 | 0 | SIMULTANEOUS MAXIMUM DEMAND (BULK) | =
STUDY AREA 2, BLOCK 9
[16 empty] | Power Factor | kVA
LOAD | NO. OF ESTABLISHMENTS | ESTIMATED AVERAGE AMPACITY | NUMBER OF PHASE | VOLTAGE | POWER (kW) | SIMULTANEOUS MAXIMUM DEMAND | = | 1380(0.6) | + | 655.5(0.7) | + | 0(0.65) | = | 728.2808 | kW | 0.9 | 809.2009 | USE 1 - 1000 kVA TRANSFORMER | 1000
Residential Load | 150 | 40 | 1 | 230 | 1380 |  |  | 2 |  | 1.46 |  | 0.86
Commercial Load | 30 | 95 | 1 | 230 | 655.5
Industrial Load | 0 | 0 | 0 | 0 | 0 | SIMULTANEOUS MAXIMUM DEMAND (BULK) | =
STUDY AREA 2, BLOCK 10
[16 empty] | Power Factor | kVA
LOAD | NO. OF ESTABLISHMENTS | ESTIMATED AVERAGE AMPACITY | NUMBER OF PHASE | VOLTAGE | POWER (kW) | SIMULTANEOUS MAXIMUM DEMAND | = | 966(0.6) | + | 258.75(0.7) | + | 0(0.65) | = | 413.8582 | kW | 0.9 | 459.8425 | USE 1 - 500 kVA TRANSFORMER | 500
Residential Load | 140 | 30 | 1 | 230 | 966 |  |  | 2 |  | 1.46 |  | 0.86
Commercial Load | 15 | 75 | 1 | 230 | 258.75
Industrial Load | 0 | 0 | 0 | 0 | 0 | SIMULTANEOUS MAXIMUM DEMAND (BULK) | =
STUDY AREA 2, BLOCK 11
[16 empty] | Power Factor | kVA
LOAD | NO. OF ESTABLISHMENTS | ESTIMATED AVERAGE AMPACITY | NUMBER OF PHASE | VOLTAGE | POWER (kW) | SIMULTANEOUS MAXIMUM DEMAND | = | 598(0.6) | + | 149.5(0.7) | + | 0(0.65) | = | 251.0781 | kW | 0.9 | 278.9756 | USE 1 - 300 kVA TRANSFORMER | 300
Residential Load | 130 | 20 | 1 | 230 | 598 |  |  | 2 |  | 1.46 |  | 0.86
Commercial Load | 10 | 65 | 1 | 230 | 149.5
Industrial Load | 0 | 0 | 0 | 0 | 0 | SIMULTANEOUS MAXIMUM DEMAND (BULK) | =
STUDY AREA 2, BLOCK 12
[16 empty] | Power Factor | kVA
LOAD | NO. OF ESTABLISHMENTS | ESTIMATED AVERAGE AMPACITY | NUMBER OF PHASE | VOLTAGE | POWER (kW) | SIMULTANEOUS MAXIMUM DEMAND | = | 1380(0.6) | + | 488.75(0.7) | + | 0(0.65) | = | 648.3322 | kW | 0.9 | 720.3691 | USE 1 - 800 kVA TRANSFORMER | 800
Residential Load | 150 | 40 | 1 | 230 | 1380 |  |  | 2 |  | 1.46 |  | 0.86
Commercial Load | 25 | 85 | 1 | 230 | 488.75
Industrial Load | 0 | 0 | 0 | 0 | 0 | SIMULTANEOUS MAXIMUM DEMAND (BULK) | =
STUDY AREA 2, BLOCK 13
[16 empty] | Power Factor | kVA
LOAD | NO. OF ESTABLISHMENTS | ESTIMATED AVERAGE AMPACITY | NUMBER OF PHASE | VOLTAGE | POWER (kW) | SIMULTANEOUS MAXIMUM DEMAND | = | 736(0.6) | + | 224.25(0.7) | + | 0(0.65) | = | 328.3171 | kW | 0.9 | 364.7968 | USE 1 - 450 kVA TRANSFORMER | 450
Residential Load | 80 | 40 | 1 | 230 | 736 |  |  | 2 |  | 1.46 |  | 0.86
Commercial Load | 15 | 65 | 1 | 230 | 224.25
Industrial Load | 0 | 0 | 0 | 0 | 0 | SIMULTANEOUS MAXIMUM DEMAND (BULK) | =
STUDY AREA 2, BLOCK 14
[16 empty] | Power Factor | kVA
LOAD | NO. OF ESTABLISHMENTS | ESTIMATED AVERAGE AMPACITY | NUMBER OF PHASE | VOLTAGE | POWER (kW) | SIMULTANEOUS MAXIMUM DEMAND | = | 230(0.6) | + | 74.75(0.7) | + | 0(0.65) | = | 104.839 | kW | 0.9 | 116.4878 | USE 1 - 150 kVA TRANSFORMER | 800
Residential Load | 50 | 20 | 1 | 230 | 230 |  |  | 2 |  | 1.46 |  | 0.86
Commercial Load | 5 | 65 | 1 | 230 | 74.75
Industrial Load (Bulk) | 1 | 600 | 3 | 2300 | 2390.2301 | SIMULTANEOUS MAXIMUM DEMAND (BULK) | = | 2390(0.7) | [5 empty] | 1859.0679 | kVA |  |  | USE 1 - 2000 kVA TRANSFORMER | 2000
0.9
STUDY AREA 2, BLOCK 15
[16 empty] | Power Factor | kVA
LOAD | NO. OF ESTABLISHMENTS | ESTIMATED AVERAGE AMPACITY | NUMBER OF PHASE | VOLTAGE | POWER (kW) | SIMULTANEOUS MAXIMUM DEMAND | = | 276(0.6) | + | 149.5(0.7) | + | 0(0.65) | = | 154.4781 | kW | 0.9 | 171.6423 | USE 1 - 225 kVA TRANSFORMER | 225
Residential Load | 80 | 15 | 1 | 230 | 276 |  |  | 2 |  | 1.46 |  | 0.86
Commercial Load | 10 | 65 | 1 | 230 | 149.5
Industrial Load | 0 | 0 | 0 | 0 | 0 | SIMULTANEOUS MAXIMUM DEMAND (BULK) | =

## STUDY AREA 3
STUDY AREA 3, BLOCK 1
[16 empty] | Power Factor | kVA | TRANSFORMER SIZE
LOAD | NO. OF ESTABLISHMENTS | ESTIMATED AVERAGE AMPACITY | NUMBER OF PHASE | VOLTAGE | POWER (kW) | SIMULTANEOUS MAXIMUM DEMAND | = | 736(0.6) | + | 80.5(0.7) | + | 0(0.65) | = | 259.3959 | kW | 0.9 | 288.2177 | USE 1 - 300 kVA TRANSFORMER | 300
Residential Load | 160 | 20 | 1 | 230 | 736 |  |  | 2 |  | 1.46 |  | 0.86 | [7 empty] | LOAD
Commercial Load | 5 | 70 | 1 | 230 | 80.5 | [14 empty] | Residential Load | 7820
Industrial Load | 0 | 0 | 0 | 0 | 0 | SIMULTANEOUS MAXIMUM DEMAND (BULK) | = | [12 empty] | Commercial Load | 3070.5
[20 empty] | Industrial Load | 0
STUDY AREA 3, BLOCK 2
[16 empty] | Power Factor | kVA
LOAD | NO. OF ESTABLISHMENTS | ESTIMATED AVERAGE AMPACITY | NUMBER OF PHASE | VOLTAGE | POWER (kW) | SIMULTANEOUS MAXIMUM DEMAND | = | 805(0.6) | + | 172.5(0.7) | + | 0(0.65) | = | 324.2055 | kW | 0.9 | 360.2283 | USE 1 - 450 kVA TRANSFORMER | 450
Residential Load | 140 | 25 | 1 | 230 | 805 |  |  | 2 |  | 1.46 |  | 0.86
Commercial Load | 10 | 75 | 1 | 230 | 172.5
Industrial Load | 0 | 0 | 0 | 0 | 0 | SIMULTANEOUS MAXIMUM DEMAND (BULK) | =
STUDY AREA 3, BLOCK 3
[16 empty] | Power Factor | kVA
LOAD | NO. OF ESTABLISHMENTS | ESTIMATED AVERAGE AMPACITY | NUMBER OF PHASE | VOLTAGE | POWER (kW) | SIMULTANEOUS MAXIMUM DEMAND | = | 575(0.6) | + | 368(0.7) | + | 0(0.65) | = | 348.9384 | kW | 0.9 | 387.7093 | USE 1 - 450 kVA TRANSFORMER | 450
Residential Load | 100 | 25 | 1 | 230 | 575 |  |  | 2 |  | 1.46 |  | 0.86
Commercial Load | 20 | 80 | 1 | 230 | 368
Industrial Load | 0 | 0 | 0 | 0 | 0 | SIMULTANEOUS MAXIMUM DEMAND (BULK) | =
STUDY AREA 3, BLOCK 4
[16 empty] | Power Factor | kVA
LOAD | NO. OF ESTABLISHMENTS | ESTIMATED AVERAGE AMPACITY | NUMBER OF PHASE | VOLTAGE | POWER (kW) | SIMULTANEOUS MAXIMUM DEMAND | = | 241.5(0.6) | + | 149.5(0.7) | + | 0(0.65) | = | 144.1281 | kW | 0.9 | 160.1423 | USE 1 - 225 kVA TRANSFORMER | 225
Residential Load | 70 | 15 | 1 | 230 | 241.5 |  |  | 2 |  | 1.46 |  | 0.86
Commercial Load | 10 | 65 | 1 | 230 | 149.5
Industrial Load | 0 | 0 | 0 | 0 | 0 | SIMULTANEOUS MAXIMUM DEMAND (BULK) | =
STUDY AREA 3, BLOCK 5
[16 empty] | Power Factor | kVA
LOAD | NO. OF ESTABLISHMENTS | ESTIMATED AVERAGE AMPACITY | NUMBER OF PHASE | VOLTAGE | POWER (kW) | SIMULTANEOUS MAXIMUM DEMAND | = | 460(0.6) | + | 74.75(0.7) | + | 0(0.65) | = | 173.839 | kW | 0.9 | 193.1545 | USE 1 - 225 kVA TRANSFORMER | 225
Residential Load | 80 | 25 | 1 | 230 | 460 |  |  | 2 |  | 1.46 |  | 0.86
Commercial Load | 5 | 65 | 1 | 230 | 74.75
Industrial Load | 0 | 0 | 0 | 0 | 0 | SIMULTANEOUS MAXIMUM DEMAND (BULK) | =
STUDY AREA 3, BLOCK 6
[16 empty] | Power Factor | kVA
LOAD | NO. OF ESTABLISHMENTS | ESTIMATED AVERAGE AMPACITY | NUMBER OF PHASE | VOLTAGE | POWER (kW) | SIMULTANEOUS MAXIMUM DEMAND | = | 483(0.6) | + | 258.75(0.7) | + | 0(0.65) | = | 268.9582 | kW | 0.9 | 298.8425 | USE 1 - 300 kVA TRANSFORMER | 300
Residential Load | 70 | 30 | 1 | 230 | 483 |  |  | 2 |  | 1.46 |  | 0.86
Commercial Load | 15 | 75 | 1 | 230 | 258.75
Industrial Load | 0 | 0 | 0 | 0 | 0 | SIMULTANEOUS MAXIMUM DEMAND (BULK) | =
STUDY AREA 3, BLOCK 7
[16 empty] | Power Factor | kVA
LOAD | NO. OF ESTABLISHMENTS | ESTIMATED AVERAGE AMPACITY | NUMBER OF PHASE | VOLTAGE | POWER (kW) | SIMULTANEOUS MAXIMUM DEMAND | = | 414(0.6) | + | 224.25(0.7) | + | 0(0.65) | = | 231.7171 | kW | 0.9 | 257.4635 | USE 1 - 300 kVA TRANSFORMER | 300
Residential Load | 120 | 15 | 1 | 230 | 414 |  |  | 2 |  | 1.46 |  | 0.86
Commercial Load | 15 | 65 | 1 | 230 | 224.25
Industrial Load | 0 | 0 | 0 | 0 | 0 | SIMULTANEOUS MAXIMUM DEMAND (BULK) | =
STUDY AREA 3, BLOCK 8
[16 empty] | Power Factor | kVA
LOAD | NO. OF ESTABLISHMENTS | ESTIMATED AVERAGE AMPACITY | NUMBER OF PHASE | VOLTAGE | POWER (kW) | SIMULTANEOUS MAXIMUM DEMAND | = | 460(0.6) | + | 161(0.7) | + | 0(0.65) | = | 215.1918 | kW | 0.9 | 239.102 | USE 1 - 300 kVA TRANSFORMER | 300
Residential Load | 100 | 20 | 1 | 230 | 460 |  |  | 2 |  | 1.46 |  | 0.86
Commercial Load | 10 | 70 | 1 | 230 | 161
Industrial Load | 0 | 0 | 0 | 0 | 0 | SIMULTANEOUS MAXIMUM DEMAND (BULK) | =
STUDY AREA 3, BLOCK 9
[16 empty] | Power Factor | kVA
LOAD | NO. OF ESTABLISHMENTS | ESTIMATED AVERAGE AMPACITY | NUMBER OF PHASE | VOLTAGE | POWER (kW) | SIMULTANEOUS MAXIMUM DEMAND | = | 690(0.6) | + | 414(0.7) | + | 0(0.65) | = | 405.4932 | kW | 0.9 | 450.5479 | USE 1 - 500 kVA TRANSFORMER | 500
Residential Load | 120 | 25 | 1 | 230 | 690 |  |  | 2 |  | 1.46 |  | 0.86
Commercial Load | 20 | 90 | 1 | 230 | 414
Commercial Load (Bulk) | 1 | 4000 | 3 | 400 | 2771.2813 | SIMULTANEOUS MAXIMUM DEMAND (BULK) | = | 2771(0.7) | [5 empty] | 2155.441 | kVA |  |  | USE 1 - 2500 kVA TRANSFORMER | 2500
Industrial Load | 0 | 0 | 0 | 0 | 0 |  |  | 0.9
STUDY AREA 3, BLOCK 10
[16 empty] | Power Factor | kVA
LOAD | NO. OF ESTABLISHMENTS | ESTIMATED AVERAGE AMPACITY | NUMBER OF PHASE | VOLTAGE | POWER (kW) | SIMULTANEOUS MAXIMUM DEMAND | = | 414(0.6) | + | 74.75(0.7) | + | 0(0.65) | = | 160.039 | kW | 0.9 | 177.8212 | USE 1 - 225 kVA TRANSFORMER | 225
Residential Load | 90 | 20 | 1 | 230 | 414 |  |  | 2 |  | 1.46 |  | 0.86
Commercial Load | 5 | 65 | 1 | 230 | 74.75
Industrial Load | 0 | 0 | 0 | 0 | 0 | SIMULTANEOUS MAXIMUM DEMAND (BULK) | =
STUDY AREA 3, BLOCK 11
[16 empty] | Power Factor | kVA
LOAD | NO. OF ESTABLISHMENTS | ESTIMATED AVERAGE AMPACITY | NUMBER OF PHASE | VOLTAGE | POWER (kW) | SIMULTANEOUS MAXIMUM DEMAND | = | 414(0.6) | + | 74.75(0.7) | + | 0(0.65) | = | 160.039 | kW | 0.9 | 177.8212 | USE 1 - 225 kVA TRANSFORMER | 225
Residential Load | 90 | 20 | 1 | 230 | 414 |  |  | 2 |  | 1.46 |  | 0.86
Commercial Load | 5 | 65 | 1 | 230 | 74.75
Industrial Load | 0 | 0 | 0 | 0 | 0 | SIMULTANEOUS MAXIMUM DEMAND (BULK) | =
STUDY AREA 3, BLOCK 12
[16 empty] | Power Factor | kVA
LOAD | NO. OF ESTABLISHMENTS | ESTIMATED AVERAGE AMPACITY | NUMBER OF PHASE | VOLTAGE | POWER (kW) | SIMULTANEOUS MAXIMUM DEMAND | = | 483(0.6) | + | 258.75(0.7) | + | 0(0.65) | = | 268.9582 | kW | 0.9 | 298.8425 | USE 1 - 300 kVA TRANSFORMER | 300
Residential Load | 70 | 30 | 1 | 230 | 483 |  |  | 2 |  | 1.46 |  | 0.86
Commercial Load | 15 | 75 | 1 | 230 | 258.75
Commercial Load (Bulk) | 1 | 4300 | 3 | 400 | 2979.1274 | SIMULTANEOUS MAXIMUM DEMAND (BULK) | = | 2979(0.7) | [5 empty] | 2317.0991 | kVA |  |  | USE 1 - 2500 kVA TRANSFORMER | 2500
Industrial Load | 0 | 0 | 0 | 0 | 0 |  |  | 0.9
STUDY AREA 3, BLOCK 13
[16 empty] | Power Factor | kVA
LOAD | NO. OF ESTABLISHMENTS | ESTIMATED AVERAGE AMPACITY | NUMBER OF PHASE | VOLTAGE | POWER (kW) | SIMULTANEOUS MAXIMUM DEMAND | = | 598(0.6) | + | 74.75(0.7) | + | 0(0.65) | = | 215.239 | kW | 0.9 | 239.1545 | USE 1 - 300 kVA TRANSFORMER | 300
Residential Load | 130 | 20 | 1 | 230 | 598 |  |  | 2 |  | 1.46 |  | 0.86
Commercial Load | 5 | 65 | 1 | 230 | 74.75
Industrial Load | 0 | 0 | 0 | 0 | 0 | SIMULTANEOUS MAXIMUM DEMAND (BULK) | =
STUDY AREA 3, BLOCK 14
[16 empty] | Power Factor | kVA
LOAD | NO. OF ESTABLISHMENTS | ESTIMATED AVERAGE AMPACITY | NUMBER OF PHASE | VOLTAGE | POWER (kW) | SIMULTANEOUS MAXIMUM DEMAND | = | 483(0.6) | + | 293.25(0.7) | + | 0(0.65) | = | 285.4993 | kW | 0.9 | 317.2215 | USE 1 - 450 kVA TRANSFORMER | 450
Residential Load | 70 | 30 | 1 | 230 | 483 |  |  | 2 |  | 1.46 |  | 0.86
Commercial Load | 15 | 85 | 1 | 230 | 293.25
Industrial Load | 0 | 0 | 0 | 0 | 0 | SIMULTANEOUS MAXIMUM DEMAND (BULK) | =
STUDY AREA 3, BLOCK 15
[16 empty] | Power Factor | kVA
LOAD | NO. OF ESTABLISHMENTS | ESTIMATED AVERAGE AMPACITY | NUMBER OF PHASE | VOLTAGE | POWER (kW) | SIMULTANEOUS MAXIMUM DEMAND | = | 563.5(0.6) | + | 391(0.7) | + | 0(0.65) | = | 356.5158 | kW | 0.9 | 396.1286 | USE 1 - 450 kVA TRANSFORMER | 450
Residential Load | 70 | 35 | 1 | 230 | 563.5 |  |  | 2 |  | 1.46 |  | 0.86
Commercial Load | 20 | 85 | 1 | 230 | 391
Industrial Load | 0 | 0 | 0 | 0 | 0 | SIMULTANEOUS MAXIMUM DEMAND (BULK) | =

## STUDY AREA 4
STUDY AREA 4, BLOCK 1
[16 empty] | Power Factor | kVA | TRANSFORMER SIZE
LOAD | NO. OF ESTABLISHMENTS | ESTIMATED AVERAGE AMPACITY | NUMBER OF PHASE | VOLTAGE | POWER (kW) | SIMULTANEOUS MAXIMUM DEMAND | = | 460(0.6) | + | 517.5(0.7) | + | 0(0.65) | = | 386.1164 | kW | 0.9 | 429.0183 | USE 1 - 450 kVA TRANSFORMER | 450
Residential Load | 50 | 40 | 1 | 230 | 460 |  |  | 2 |  | 1.46 |  | 0.86 | [7 empty] | LOAD
Commercial Load | 25 | 90 | 1 | 230 | 517.5 | [14 empty] | Residential Load | 8619.25
Commercial Load (Bulk) | 1 | 4000 | 3 | 400 | 2771.2813 | SIMULTANEOUS MAXIMUM DEMAND (BULK) | = | 2771(0.7) | [5 empty] | 2155.441 | kVA |  |  | USE 1 - 2500 kVA TRANSFORMER | 2500 | Commercial Load | 4433.25
Industrial Load | 0 | 0 | 0 | 0 | 0 |  |  | 0.9 | [11 empty] | Industrial Load | 0
STUDY AREA 4, BLOCK 2
[16 empty] | Power Factor | kVA
LOAD | NO. OF ESTABLISHMENTS | ESTIMATED AVERAGE AMPACITY | NUMBER OF PHASE | VOLTAGE | POWER (kW) | SIMULTANEOUS MAXIMUM DEMAND | = | 603.75(0.6) | + | 368(0.7) | + | 0(0.65) | = | 357.5634 | kW | 0.9 | 397.2926 | USE 1 - 450 kVA TRANSFORMER | 450
Residential Load | 75 | 35 | 1 | 230 | 603.75 |  |  | 2 |  | 1.46 |  | 0.86
Commercial Load | 20 | 80 | 1 | 230 | 368
Industrial Load | 0 | 0 | 0 | 0 | 0 | SIMULTANEOUS MAXIMUM DEMAND (BULK) | =
STUDY AREA 4, BLOCK 3
[16 empty] | Power Factor | kVA
LOAD | NO. OF ESTABLISHMENTS | ESTIMATED AVERAGE AMPACITY | NUMBER OF PHASE | VOLTAGE | POWER (kW) | SIMULTANEOUS MAXIMUM DEMAND | = | 966(0.6) | + | 431.25(0.7) | + | 0(0.65) | = | 496.5637 | kW | 0.9 | 551.7374 | USE 1 - 600 kVA TRANSFORMER | 600
Residential Load | 140 | 30 | 1 | 230 | 966 |  |  | 2 |  | 1.46 |  | 0.86
Commercial Load | 25 | 75 | 1 | 230 | 431.25
Industrial Load | 0 | 0 | 0 | 0 | 0 | SIMULTANEOUS MAXIMUM DEMAND (BULK) | =
STUDY AREA 4, BLOCK 4
[16 empty] | Power Factor | kVA
LOAD | NO. OF ESTABLISHMENTS | ESTIMATED AVERAGE AMPACITY | NUMBER OF PHASE | VOLTAGE | POWER (kW) | SIMULTANEOUS MAXIMUM DEMAND | = | 402.5(0.6) | + | 149.5(0.7) | + | 0(0.65) | = | 192.4281 | kW | 0.9 | 213.809 | USE 1 - 225 kVA TRANSFORMER | 225
Residential Load | 70 | 25 | 1 | 230 | 402.5 |  |  | 2 |  | 1.46 |  | 0.86
Commercial Load | 10 | 65 | 1 | 230 | 149.5
Industrial Load | 0 | 0 | 0 | 0 | 0 | SIMULTANEOUS MAXIMUM DEMAND (BULK) | =
STUDY AREA 4, BLOCK 5
[16 empty] | Power Factor | kVA
LOAD | NO. OF ESTABLISHMENTS | ESTIMATED AVERAGE AMPACITY | NUMBER OF PHASE | VOLTAGE | POWER (kW) | SIMULTANEOUS MAXIMUM DEMAND | = | 86.25(0.6) | + | 74.75(0.7) | + | 0(0.65) | = | 61.714 | kW | 0.9 | 68.5712 | USE 1 - 75 kVA TRANSFORMER | 75
Residential Load | 25 | 15 | 1 | 230 | 86.25 |  |  | 2 |  | 1.46 |  | 0.86
Commercial Load | 5 | 65 | 1 | 230 | 74.75
Industrial Load | 0 | 0 | 0 | 0 | 0 | SIMULTANEOUS MAXIMUM DEMAND (BULK) | =
STUDY AREA 4, BLOCK 6
[16 empty] | Power Factor | kVA
LOAD | NO. OF ESTABLISHMENTS | ESTIMATED AVERAGE AMPACITY | NUMBER OF PHASE | VOLTAGE | POWER (kW) | SIMULTANEOUS MAXIMUM DEMAND | = | 86.25(0.6) | + | 74.75(0.7) | + | 0(0.65) | = | 61.714 | kW | 0.9 | 68.5712 | USE 1 - 75 kVA TRANSFORMER | 75
Residential Load | 25 | 15 | 1 | 230 | 86.25 |  |  | 2 |  | 1.46 |  | 0.86
Commercial Load | 5 | 65 | 1 | 230 | 74.75
Industrial Load | 0 | 0 | 0 | 0 | 0 | SIMULTANEOUS MAXIMUM DEMAND (BULK) | =
STUDY AREA 4, BLOCK 7
[16 empty] | Power Factor | kVA
LOAD | NO. OF ESTABLISHMENTS | ESTIMATED AVERAGE AMPACITY | NUMBER OF PHASE | VOLTAGE | POWER (kW) | SIMULTANEOUS MAXIMUM DEMAND | = | 805(0.6) | + | 586.5(0.7) | + | 0(0.65) | = | 522.6986 | kW | 0.9 | 580.7763 | USE 1 - 600 kVA TRANSFORMER | 600
Residential Load | 100 | 35 | 1 | 230 | 805 |  |  | 2 |  | 1.46 |  | 0.86
Commercial Load | 30 | 85 | 1 | 230 | 586.5
Commercial Load (Bulk) | 1 | 4000 | 3 | 400 | 2771.2813 | SIMULTANEOUS MAXIMUM DEMAND (BULK) | = | 2771(0.7) | [5 empty] | 2155.441 | kVA |  |  | USE 1 - 2500 kVA TRANSFORMER | 2500
Industrial Load | 0 | 0 | 0 | 0 | 0 |  |  | 0.9
STUDY AREA 4, BLOCK 8
[16 empty] | Power Factor | kVA
LOAD | NO. OF ESTABLISHMENTS | ESTIMATED AVERAGE AMPACITY | NUMBER OF PHASE | VOLTAGE | POWER (kW) | SIMULTANEOUS MAXIMUM DEMAND | = | 966(0.6) | + | 345(0.7) | + | 0(0.65) | = | 455.211 | kW | 0.9 | 505.79 | USE 1 - 600 kVA TRANSFORMER | 600
Residential Load | 120 | 35 | 1 | 230 | 966 |  |  | 2 |  | 1.46 |  | 0.86
Commercial Load | 20 | 75 | 1 | 230 | 345
Industrial Load | 0 | 0 | 0 | 0 | 0 | SIMULTANEOUS MAXIMUM DEMAND (BULK) | =
STUDY AREA 4, BLOCK 9
[16 empty] | Power Factor | kVA
LOAD | NO. OF ESTABLISHMENTS | ESTIMATED AVERAGE AMPACITY | NUMBER OF PHASE | VOLTAGE | POWER (kW) | SIMULTANEOUS MAXIMUM DEMAND | = | 897(0.6) | + | 431.25(0.7) | + | 0(0.65) | = | 475.8637 | kW | 0.9 | 528.7374 | USE 1 - 600 kVA TRANSFORMER | 600
Residential Load | 130 | 30 | 1 | 230 | 897 |  |  | 2 |  | 1.46 |  | 0.86
Commercial Load | 25 | 75 | 1 | 230 | 431.25
Industrial Load | 0 | 0 | 0 | 0 | 0 | SIMULTANEOUS MAXIMUM DEMAND (BULK) | =
STUDY AREA 4, BLOCK 10
[16 empty] | Power Factor | kVA
LOAD | NO. OF ESTABLISHMENTS | ESTIMATED AVERAGE AMPACITY | NUMBER OF PHASE | VOLTAGE | POWER (kW) | SIMULTANEOUS MAXIMUM DEMAND | = | 172.5(0.6) | + | 149.5(0.7) | + | 0(0.65) | = | 123.4281 | kW | 0.9 | 137.1423 | USE 1 - 150 kVA TRANSFORMER | 150
Residential Load | 50 | 15 | 1 | 230 | 172.5 |  |  | 2 |  | 1.46 |  | 0.86
Commercial Load | 10 | 65 | 1 | 230 | 149.5
Industrial Load | 0 | 0 | 0 | 0 | 0 | SIMULTANEOUS MAXIMUM DEMAND (BULK) | =
STUDY AREA 4, BLOCK 11
[16 empty] | Power Factor | kVA
LOAD | NO. OF ESTABLISHMENTS | ESTIMATED AVERAGE AMPACITY | NUMBER OF PHASE | VOLTAGE | POWER (kW) | SIMULTANEOUS MAXIMUM DEMAND | = | 172.5(0.6) | + | 74.75(0.7) | + | 0(0.65) | = | 87.589 | kW | 0.9 | 97.3212 | USE 1 - 112.5 kVA TRANSFORMER | 112.5
Residential Load | 50 | 15 | 1 | 230 | 172.5 |  |  | 2 |  | 1.46 |  | 0.86
Commercial Load | 5 | 65 | 1 | 230 | 74.75
Industrial Load | 0 | 0 | 0 | 0 | 0 | SIMULTANEOUS MAXIMUM DEMAND (BULK) | =
STUDY AREA 4, BLOCK 12
[16 empty] | Power Factor | kVA
LOAD | NO. OF ESTABLISHMENTS | ESTIMATED AVERAGE AMPACITY | NUMBER OF PHASE | VOLTAGE | POWER (kW) | SIMULTANEOUS MAXIMUM DEMAND | = | 172.5(0.6) | + | 74.75(0.7) | + | 0(0.65) | = | 87.589 | kW | 0.9 | 97.3212 | USE 1 - 112.5 kVA TRANSFORMER | 112.5
Residential Load | 50 | 15 | 1 | 230 | 172.5 |  |  | 2 |  | 1.46 |  | 0.86
Commercial Load | 5 | 65 | 1 | 230 | 74.75
Industrial Load | 0 | 0 | 0 | 0 | 0 | SIMULTANEOUS MAXIMUM DEMAND (BULK) | =
STUDY AREA 4, BLOCK 13
[16 empty] | Power Factor | kVA
LOAD | NO. OF ESTABLISHMENTS | ESTIMATED AVERAGE AMPACITY | NUMBER OF PHASE | VOLTAGE | POWER (kW) | SIMULTANEOUS MAXIMUM DEMAND | = | 724.5(0.6) | + | 517.5(0.7) | + | 0(0.65) | = | 465.4664 | kW | 0.9 | 517.1849 | USE 1 - 600 kVA TRANSFORMER | 600
Residential Load | 90 | 35 | 1 | 230 | 724.5 |  |  | 2 |  | 1.46 |  | 0.86
Commercial Load | 25 | 90 | 1 | 230 | 517.5
Industrial Load | 0 | 0 | 0 | 0 | 0 | SIMULTANEOUS MAXIMUM DEMAND (BULK) | =
STUDY AREA 4, BLOCK 14
[16 empty] | Power Factor | kVA
LOAD | NO. OF ESTABLISHMENTS | ESTIMATED AVERAGE AMPACITY | NUMBER OF PHASE | VOLTAGE | POWER (kW) | SIMULTANEOUS MAXIMUM DEMAND | = | 828(0.6) | + | 322(0.7) | + | 0(0.65) | = | 402.7836 | kW | 0.9 | 447.5373 | USE 1 - 450 kVA TRANSFORMER | 450
Residential Load | 120 | 30 | 1 | 230 | 828 |  |  | 2 |  | 1.46 |  | 0.86
Commercial Load | 20 | 70 | 1 | 230 | 322
Industrial Load | 0 | 0 | 0 | 0 | 0 | SIMULTANEOUS MAXIMUM DEMAND (BULK) | =
STUDY AREA 3, BLOCK 15
[16 empty] | Power Factor | kVA
LOAD | NO. OF ESTABLISHMENTS | ESTIMATED AVERAGE AMPACITY | NUMBER OF PHASE | VOLTAGE | POWER (kW) | SIMULTANEOUS MAXIMUM DEMAND | = | 1104(0.6) | + | 241.5(0.7) | + | 0(0.65) | = | 446.9877 | kW | 0.9 | 496.653 | USE 1 - 500 kVA TRANSFORMER | 500
Residential Load | 160 | 30 | 1 | 230 | 1104 |  |  | 2 |  | 1.46 |  | 0.86
Commercial Load | 15 | 70 | 1 | 230 | 241.5
Industrial Load | 0 | 0 | 0 | 0 | 0 | SIMULTANEOUS MAXIMUM DEMAND (BULK) | =
STUDY AREA 4, BLOCK 16
[16 empty] | Power Factor | kVA
LOAD | NO. OF ESTABLISHMENTS | ESTIMATED AVERAGE AMPACITY | NUMBER OF PHASE | VOLTAGE | POWER (kW) | SIMULTANEOUS MAXIMUM DEMAND | = | 172.5(0.6) | + | 74.75(0.7) | + | 0(0.65) | = | 87.589 | kW | 0.9 | 97.3212 | USE 1 - 112.5 kVA TRANSFORMER | 112.5
Residential Load | 50 | 15 | 1 | 230 | 172.5 |  |  | 2 |  | 1.46 |  | 0.86
Commercial Load | 5 | 65 | 1 | 230 | 74.75
Industrial Load | 0 | 0 | 0 | 0 | 0 | SIMULTANEOUS MAXIMUM DEMAND (BULK) | =

## FEEDER AND SUBSTATION
[15 empty] | Time | Residential Load | Commercial Load | Industrial Load | Combined |  | residential |  | commercial |  |  | Month | Residential (MWh) | Commercial (MWh) | Industrial (MWh) | Combined (MWh)
FEEDERS | LOAD SIZE | UNIT |  |  | FEEDER | BULK USER | LOAD SIZE | UNIT | SUBSTATION SIZE | UNIT | POWER PLANT SIZE | UNIT | LOAD |  | 0:00 | 13431.5741 | 3505.9416 | 3879.794 | 20817.3097 | 0:00 | 10 | 0:00 | 5 | LOAD | Power (kW) | January | 21825.55 | 7260.23 | 2885.79 | 32875
1 | 5136.8956 | kVA |  |  | 1 | 11 | 1616.5808 | kVA | 13960.143 | kVA | 27093.304 | kVA | Residential Load | 36265.25 | 1:00 | 12088.4167 | 2804.7533 | 3879.794 | 18772.9639 | 1:00 | 9 | 1:00 | 4 | Residential Load | 36265.25 | February | 19713.4 | 6557.78 | 2606.52 | 29694
2 | 4325.1364 | kVA |  |  | 1 | 12 | 1562.6947 | kVA | Substation Transformer Size |  |  |  | Commercial Load | 30151.0976 | 2:00 | 10745.2593 | 2804.7533 | 3879.794 | 17429.8065 | 2:00 | 8 | 2:00 | 4 | Commercial Load | 30151.0976 | March | 21825.55 | 7260.23 | 2885.79 | 32875
3 | 3263.3825 | kVA |  |  | 2 | 21 | 2020.7259 | kVA |  |  |  |  | Industrial Load | 3879.7938 | 3:00 | 10745.2593 | 2103.5649 | 3879.794 | 16728.6182 | 3:00 | 8 | 3:00 | 3 | Industrial Load | 3879.7938 | April | 21121.4 | 7026 | 2792.7 | 31814
4 | 4026.7571 | kVA |  |  | 2 | 22 | 1859.0679 | kVA | [6 empty] | 4:00 | 12088.4167 | 2103.5649 | 3879.794 | 18071.7756 | 4:00 | 9 | 4:00 | 3 |  |  | May | 21825.55 | 7260.23 | 2885.79 | 32875
[5 empty] | 3 | 31 | 2155.441 | kVA | [6 empty] | 5:00 | 13431.5741 | 2804.7533 | 3879.794 | 20116.1213 | 5:00 | 10 | 5:00 | 4 |  |  | June | 21121.4 | 7026 | 2792.7 | 31814
[5 empty] | 3 | 32 | 2317.0991 | kVA | [6 empty] | 6:00 | 18804.2037 | 7011.8832 | 3879.794 | 29695.8809 | 6:00 | 14 | 6:00 | 10 |  |  | July | 21825.55 | 7260.23 | 2885.79 | 32875
[5 empty] | 4 | 41 | 2155.441 | kVA | [6 empty] | 7:00 | 24176.8333 | 14023.7663 | 3879.794 | 42080.3936 | 7:00 | 18 | 7:00 | 20 |  |  | August | 21825.55 | 7260.23 | 2885.79 | 32875
[5 empty] | 4 | 42 | 2155.441 | kVA | [6 empty] | 8:00 | 26863.1481 | 21035.6495 | 3879.794 | 51778.5916 | 8:00 | 20 | 8:00 | 30 |  |  | September | 21121.4 | 7026 | 2792.7 | 31814
[15 empty] | 9:00 | 25519.9907 | 24541.5911 | 3879.794 | 53941.3758 | 9:00 | 19 | 9:00 | 35 |  |  | October | 21825.55 | 7260.23 | 2885.79 | 32875
Row Labels | Sum of LOAD SIZE | Total Load | [12 empty] | 10:00 | 22833.6759 | 28047.5326 | 3879.794 | 54761.0026 | 10:00 | 17 | 10:00 | 40 |  |  | November | 21121.4 | 7026 | 2792.7 | 31814
1 | 3179.2755 | 8316.171 | [12 empty] | 11:00 | 21490.5185 | 29449.9093 | 3879.794 | 54820.2218 | 11:00 | 16 | 11:00 | 42 |  |  | December | 21825.55 | 7260.23 | 2885.79 | 32875
2 | 3879.7938 | 8204.9302 | [12 empty] | 12:00 | 20147.3611 | 30151.0976 | 3879.794 | 54178.2527 | 12:00 | 15 | 12:00 | 43
3 | 4472.5401 | 7735.9226 | [12 empty] | 13:00 | 20147.3611 | 29449.9093 | 3879.794 | 53477.0644 | 13:00 | 15 | 13:00 | 42
4 | 4310.882 | 8337.6391 | [12 empty] | 14:00 | 20147.3611 | 28047.5326 | 3879.794 | 52074.6877 | 14:00 | 15 | 14:00 | 40
Grand Total | 15842.4914 | [13 empty] | 15:00 | 21490.5185 | 26645.156 | 3879.794 | 52015.4685 | 15:00 | 16 | 15:00 | 38
[15 empty] | 16:00 | 24176.8333 | 24541.5911 | 3879.794 | 52598.2184 | 16:00 | 18 | 16:00 | 35
[15 empty] | 17:00 | 26863.1481 | 21035.6495 | 3879.794 | 51778.5916 | 17:00 | 20 | 17:00 | 30
|  |  | 1 | 8316.171 | [10 empty] | 18:00 | 29549.463 | 17529.7079 | 3879.794 | 50958.9649 | 18:00 | 22 | 18:00 | 25
|  |  | 2 | 8204.9302 | [10 empty] | 19:00 | 33578.9352 | 14023.7663 | 3879.794 | 51482.4955 | 19:00 | 25 | 19:00 | 20
|  |  | 3 | 7735.9226 | [10 empty] | 20:00 | 36265.25 | 10517.8247 | 3879.794 | 50662.8687 | 20:00 | 27 | 20:00 | 15
|  |  | 4 | 8337.6391 | [10 empty] | 21:00 | 34922.0926 | 7011.8832 | 3879.794 | 45813.7698 | 21:00 | 26 | 21:00 | 10
[15 empty] | 22:00 | 29549.463 | 4207.1299 | 3879.794 | 37636.3869 | 22:00 | 22 | 22:00 | 6
[15 empty] | 23:00 | 13431.5741 | 3505.9416 | 3879.794 | 20817.3097 | 23:00 | 10 | 23:00 | 5
[15 empty] | Average | 21770.343 | 14871.0355 | 3879.794 | 40521.1725
[15 empty] | Load Factor | 0.60031 | 0.49322 | 1 | 0.73916 | max | 27 | max | 43

## POWERPLANT
Load Type | Fuel Type | Capacity |  | Efficiency
|  | Installed(kVA) | Dependable(kVA)
Base Load | Coal Fired | 35000 | 32900 | 0.94
Peak Load | Solar | 30000 | 24000 | 0.8

## BREAKERS
Vprimary | 460 | [7 empty] | Vprimary | 460 | [7 empty] | Vprimary | 460 | [7 empty] | Vprimary | 460
Vsecondary | 230 | [7 empty] | Vsecondary | 230 | [7 empty] | Vsecondary | 230 | [7 empty] | Vsecondary | 230
STUDY AREA 1 | [8 empty] | STUDY AREA 2 | [8 empty] | STUDY AREA 3 | [8 empty] | STUDY AREA 4
| HIGH VOLTAGE | [8 empty] | HIGH VOLTAGE | [8 empty] | HIGH VOLTAGE | [8 empty] | HIGH VOLTAGE
| kVA | IFLC(HV) | CB=1.25*IFLC(HV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  | kVA | IFLC(HV) | CB=1.25*IFLC(HV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  | kVA | IFLC(HV) | CB=1.25*IFLC(HV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  | kVA | IFLC(HV) | CB=1.25*IFLC(HV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA)
TB1= | 300 | 376.5328 | 470.666 | 500 | MCCB | 4% | 9413.3196 | 15-18 | TB1= | 800 | 1004.0874 | 1255.1093 | 1600 | MCCB | 6% | 16734.7904 | 25-35 | TB1= | 300 | 376.5328 | 470.666 | 500 | MCCB | 4% | 9413.3196 | 15-18 | TB1= | 450 | 564.7992 | 705.999 | 800 | MCCB | 5% | 11295.9835 | 15-18
|  | IFLC(LV) | CB=1.25*IFLC(LV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  |  | IFLC(LV) | CB=1.25*IFLC(LV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  |  | IFLC(LV) | CB=1.25*IFLC(LV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  |  | IFLC(LV) | CB=1.25*IFLC(LV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA)
|  | 753.0656 | 941.332 | 1000 | MCCB | 4% | 18826.6392 | 25-35 |  |  | 2008.1748 | 2510.2186 | 3000 | MCCB | 6% | 33469.5808 | 60 |  |  | 753.0656 | 941.332 | 1000 | MCCB | 4% | 18826.6392 | 25-35 |  |  | 1129.5984 | 1411.9979 | 1600 | MCCB | 5% | 22591.9671 | 25-35
| kVA | IFLC(HV) | CB=1.25*IFLC(HV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  | kVA | IFLC(HV) | CB=1.25*IFLC(HV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  | kVA | IFLC(HV) | CB=1.25*IFLC(HV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  | kVA | IFLC(HV) | CB=1.25*IFLC(HV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA)
TB2= | 450 | 564.7992 | 705.999 | 800 | MCCB | 5% | 11295.9835 | 15-18 | TB2= | 450 | 564.7992 | 705.999 | 800 | MCCB | 5% | 11295.9835 | 15-18 | TB2= | 450 | 564.7992 | 705.999 | 800 | MCCB | 5% | 11295.9835 | 15-18 | TB2= | 450 | 564.7992 | 705.999 | 800 | MCCB | 5% | 11295.9835 | 15-18
|  | IFLC(LV) | CB=1.25*IFLC(LV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  |  | IFLC(LV) | CB=1.25*IFLC(LV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  |  | IFLC(LV) | CB=1.25*IFLC(LV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  |  | IFLC(LV) | CB=1.25*IFLC(LV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA)
|  | 1129.5984 | 1411.9979 | 1600 | MCCB | 5% | 22591.9671 | 25-35 |  |  | 1129.5984 | 1411.9979 | 1600 | MCCB | 5% | 22591.9671 | 25-35 |  |  | 1129.5984 | 1411.9979 | 1600 | MCCB | 5% | 22591.9671 | 25-35 |  |  | 1129.5984 | 1411.9979 | 1600 | MCCB | 5% | 22591.9671 | 25-35
| kVA | IFLC(HV) | CB=1.25*IFLC(HV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  | kVA | IFLC(HV) | CB=1.25*IFLC(HV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  | kVA | IFLC(HV) | CB=1.25*IFLC(HV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  | kVA | IFLC(HV) | CB=1.25*IFLC(HV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA)
TB3= | 1000 | 1255.1093 | 1568.8866 | 1600 | MCCB | 6% | 20918.488 | 25-35 | TB3= | 112.5 | 141.1998 | 176.4997 | 200 | MCCB | 4% | 3529.9949 | 6-10 | TB3= | 450 | 564.7992 | 705.999 | 800 | MCCB | 5% | 11295.9835 | 15-18 | TB3= | 600 | 753.0656 | 941.332 | 1000 | MCCB | 5% | 15061.3114 | 25-35
|  | IFLC(LV) | CB=1.25*IFLC(LV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  |  | IFLC(LV) | CB=1.25*IFLC(LV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  |  | IFLC(LV) | CB=1.25*IFLC(LV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  |  | IFLC(LV) | CB=1.25*IFLC(LV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA)
|  | 2510.2186 | 3137.7732 | 4000 | MCCB | 6% | 41836.976 | 60 |  |  | 282.3996 | 352.9995 | 400 | MCCB | 4% | 7059.9897 | 10 |  |  | 1129.5984 | 1411.9979 | 1600 | MCCB | 5% | 22591.9671 | 25-35 |  |  | 1506.1311 | 1882.6639 | 2000 | MCCB | 5% | 30122.6227 | 60
| kVA | IFLC(HV) | CB=1.25*IFLC(HV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  | kVA | IFLC(HV) | CB=1.25*IFLC(HV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  | kVA | IFLC(HV) | CB=1.25*IFLC(HV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  | kVA | IFLC(HV) | CB=1.25*IFLC(HV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA)
TB4= | 225 | 282.3996 | 352.9995 | 400 | MCCB | 4% | 7059.9897 | 10 | TB4= | 150 | 188.2664 | 235.333 | 250 | MCCB | 4% | 4706.6598 | 10 | TB4= | 225 | 282.3996 | 352.9995 | 400 | MCCB | 4% | 7059.9897 | 10 | TB4= | 225 | 282.3996 | 352.9995 | 400 | MCCB | 4% | 7059.9897 | 10
|  | IFLC(LV) | CB=1.25*IFLC(LV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  |  | IFLC(LV) | CB=1.25*IFLC(LV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  |  | IFLC(LV) | CB=1.25*IFLC(LV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  |  | IFLC(LV) | CB=1.25*IFLC(LV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA)
|  | 564.7992 | 705.999 | 800 | MCCB | 4% | 14119.9794 | 25-35 |  |  | 376.5328 | 470.666 | 500 | MCCB | 4% | 9413.3196 | 15-18 |  |  | 564.7992 | 705.999 | 800 | MCCB | 4% | 14119.9794 | 25-35 |  |  | 564.7992 | 705.999 | 800 | MCCB | 4% | 14119.9794 | 25-35
| kVA | IFLC(HV) | CB=1.25*IFLC(HV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  | kVA | IFLC(HV) | CB=1.25*IFLC(HV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  | kVA | IFLC(HV) | CB=1.25*IFLC(HV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  | kVA | IFLC(HV) | CB=1.25*IFLC(HV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA)
TB5= | 300 | 376.5328 | 470.666 | 500 | MCCB | 4% | 9413.3196 | 15-18 | TB5= | 112.5 | 141.1998 | 176.4997 | 200 | MCCB | 4% | 3529.9949 | 6-10 | TB5= | 225 | 282.3996 | 352.9995 | 400 | MCCB | 4% | 7059.9897 | 10 | TB5= | 75 | 94.1332 | 117.6665 | 125 | MCCB | 4% | 2353.3299 | 6-10
|  | IFLC(LV) | CB=1.25*IFLC(LV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  |  | IFLC(LV) | CB=1.25*IFLC(LV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  |  | IFLC(LV) | CB=1.25*IFLC(LV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  |  | IFLC(LV) | CB=1.25*IFLC(LV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA)
|  | 753.0656 | 941.332 | 1000 | MCCB | 4% | 18826.6392 | 25-35 |  |  | 282.3996 | 352.9995 | 400 | MCCB | 4% | 7059.9897 | 10 |  |  | 564.7992 | 705.999 | 800 | MCCB | 4% | 14119.9794 | 25-35 |  |  | 188.2664 | 235.333 | 250 | MCCB | 4% | 4706.6598 | 10
| kVA | IFLC(HV) | CB=1.25*IFLC(HV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  | kVA | IFLC(HV) | CB=1.25*IFLC(HV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  | kVA | IFLC(HV) | CB=1.25*IFLC(HV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  | kVA | IFLC(HV) | CB=1.25*IFLC(HV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA)
TB6= | 450 | 564.7992 | 705.999 | 800 | MCCB | 5% | 11295.9835 | 15-18 | TB6= | 600 | 753.0656 | 941.332 | 1000 | MCCB | 5% | 15061.3114 | 25-35 | TB6= | 300 | 376.5328 | 470.666 | 500 | MCCB | 4% | 9413.3196 | 15-18 | TB6= | 75 | 94.1332 | 117.6665 | 125 | MCCB | 4% | 2353.3299 | 6-10
|  | IFLC(LV) | CB=1.25*IFLC(LV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  |  | IFLC(LV) | CB=1.25*IFLC(LV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  |  | IFLC(LV) | CB=1.25*IFLC(LV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  |  | IFLC(LV) | CB=1.25*IFLC(LV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA)
|  | 1129.5984 | 1411.9979 | 1600 | MCCB | 5% | 22591.9671 | 25-35 |  |  | 1506.1311 | 1882.6639 | 2000 | MCCB | 5% | 30122.6227 | 60 |  |  | 753.0656 | 941.332 | 1000 | MCCB | 4% | 18826.6392 | 25-35 |  |  | 188.2664 | 235.333 | 250 | MCCB | 4% | 4706.6598 | 10
| kVA | IFLC(HV) | CB=1.25*IFLC(HV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  | kVA | IFLC(HV) | CB=1.25*IFLC(HV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  | kVA | IFLC(HV) | CB=1.25*IFLC(HV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  | kVA | IFLC(HV) | CB=1.25*IFLC(HV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA)
TB7= | 450 | 564.7992 | 705.999 | 800 | MCCB | 5% | 11295.9835 | 15-18 | TB7= | 500 | 627.5546 | 784.4433 | 800 | MCCB | 5% | 12551.0928 | 25-35 | TB7= | 300 | 376.5328 | 470.666 | 500 | MCCB | 4% | 9413.3196 | 15-18 | TB7= | 600 | 753.0656 | 941.332 | 1000 | MCCB | 5% | 15061.3114 | 25-35
|  | IFLC(LV) | CB=1.25*IFLC(LV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  |  | IFLC(LV) | CB=1.25*IFLC(LV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  |  | IFLC(LV) | CB=1.25*IFLC(LV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  |  | IFLC(LV) | CB=1.25*IFLC(LV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA)
|  | 1129.5984 | 1411.9979 | 1600 | MCCB | 5% | 22591.9671 | 25-35 |  |  | 1255.1093 | 1568.8866 | 1600 | MCCB | 5% | 25102.1856 | 60 |  |  | 753.0656 | 941.332 | 1000 | MCCB | 4% | 18826.6392 | 25-35 |  |  | 1506.1311 | 1882.6639 | 2000 | MCCB | 5% | 30122.6227 | 60
| kVA | IFLC(HV) | CB=1.25*IFLC(HV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  | kVA | IFLC(HV) | CB=1.25*IFLC(HV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  | kVA | IFLC(HV) | CB=1.25*IFLC(HV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  | kVA | IFLC(HV) | CB=1.25*IFLC(HV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA)
TB8= | 800 | 1004.0874 | 1255.1093 | 1600 | MCCB | 6% | 16734.7904 | 25-35 | TB8= | 300 | 376.5328 | 470.666 | 500 | MCCB | 4% | 9413.3196 | 15-18 | TB8= | 300 | 376.5328 | 470.666 | 500 | MCCB | 4% | 9413.3196 | 15-18 | TB8= | 600 | 753.0656 | 941.332 | 1000 | MCCB | 5% | 15061.3114 | 25-35
|  | IFLC(LV) | CB=1.25*IFLC(LV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  |  | IFLC(LV) | CB=1.25*IFLC(LV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  |  | IFLC(LV) | CB=1.25*IFLC(LV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  |  | IFLC(LV) | CB=1.25*IFLC(LV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA)
|  | 2008.1748 | 2510.2186 | 3000 | MCCB | 6% | 33469.5808 | 60 |  |  | 753.0656 | 941.332 | 1000 | MCCB | 4% | 18826.6392 | 25-35 |  |  | 753.0656 | 941.332 | 1000 | MCCB | 4% | 18826.6392 | 25-35 |  |  | 1506.1311 | 1882.6639 | 2000 | MCCB | 5% | 30122.6227 | 60
| kVA | IFLC(HV) | CB=1.25*IFLC(HV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  | kVA | IFLC(HV) | CB=1.25*IFLC(HV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  | kVA | IFLC(HV) | CB=1.25*IFLC(HV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  | kVA | IFLC(HV) | CB=1.25*IFLC(HV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA)
TB9= | 300 | 376.5328 | 470.666 | 500 | MCCB | 4% | 9413.3196 | 15-18 | TB9= | 1000 | 1255.1093 | 1568.8866 | 1600 | MCCB | 6% | 20918.488 | 25-35 | TB9= | 500 | 627.5546 | 784.4433 | 800 | MCCB | 5% | 12551.0928 | 25-35 | TB9= | 600 | 753.0656 | 941.332 | 1000 | MCCB | 5% | 15061.3114 | 25-35
|  | IFLC(LV) | CB=1.25*IFLC(LV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  |  | IFLC(LV) | CB=1.25*IFLC(LV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  |  | IFLC(LV) | CB=1.25*IFLC(LV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  |  | IFLC(LV) | CB=1.25*IFLC(LV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA)
|  | 753.0656 | 941.332 | 1000 | MCCB | 4% | 18826.6392 | 25-35 |  |  | 2510.2186 | 3137.7732 | 4000 | MCCB | 6% | 41836.976 | 60 |  |  | 1255.1093 | 1568.8866 | 1600 | MCCB | 5% | 25102.1856 | 60 |  |  | 1506.1311 | 1882.6639 | 2000 | MCCB | 5% | 30122.6227 | 60
| kVA | IFLC(HV) | CB=1.25*IFLC(HV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  | kVA | IFLC(HV) | CB=1.25*IFLC(HV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  | kVA | IFLC(HV) | CB=1.25*IFLC(HV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  | kVA | IFLC(HV) | CB=1.25*IFLC(HV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA)
TB10= | 225 | 282.3996 | 352.9995 | 400 | MCCB | 4% | 7059.9897 | 10 | TB10= | 500 | 627.5546 | 784.4433 | 800 | MCCB | 5% | 12551.0928 | 25-35 | TB10= | 225 | 282.3996 | 352.9995 | 400 | MCCB | 4% | 7059.9897 | 10 | TB10= | 150 | 188.2664 | 235.333 | 250 | MCCB | 4% | 4706.6598 | 10
|  | IFLC(LV) | CB=1.25*IFLC(LV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  |  | IFLC(LV) | CB=1.25*IFLC(LV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  |  | IFLC(LV) | CB=1.25*IFLC(LV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  |  | IFLC(LV) | CB=1.25*IFLC(LV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA)
|  | 564.7992 | 705.999 | 800 | MCCB | 4% | 14119.9794 | 25-35 |  |  | 1255.1093 | 1568.8866 | 1600 | MCCB | 5% | 25102.1856 | 60 |  |  | 564.7992 | 705.999 | 800 | MCCB | 4% | 14119.9794 | 25-35 |  |  | 376.5328 | 470.666 | 500 | MCCB | 4% | 9413.3196 | 15-18
| kVA | IFLC(HV) | CB=1.25*IFLC(HV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  | kVA | IFLC(HV) | CB=1.25*IFLC(HV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  | kVA | IFLC(HV) | CB=1.25*IFLC(HV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  | kVA | IFLC(HV) | CB=1.25*IFLC(HV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA)
TB11= | 450 | 564.7992 | 705.999 | 800 | MCCB | 5% | 11295.9835 | 15-18 | TB11= | 300 | 376.5328 | 470.666 | 500 | MCCB | 4% | 9413.3196 | 15-18 | TB11= | 225 | 282.3996 | 352.9995 | 400 | MCCB | 4% | 7059.9897 | 10 | TB11= | 112.5 | 141.1998 | 176.4997 | 200 | MCCB | 4% | 3529.9949 | 6-10
|  | IFLC(LV) | CB=1.25*IFLC(LV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  |  | IFLC(LV) | CB=1.25*IFLC(LV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  |  | IFLC(LV) | CB=1.25*IFLC(LV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  |  | IFLC(LV) | CB=1.25*IFLC(LV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA)
|  | 1129.5984 | 1411.9979 | 1600 | MCCB | 5% | 22591.9671 | 25-35 |  |  | 753.0656 | 941.332 | 1000 | MCCB | 4% | 18826.6392 | 25-35 |  |  | 564.7992 | 705.999 | 800 | MCCB | 4% | 14119.9794 | 25-35 |  |  | 282.3996 | 352.9995 | 400 | MCCB | 4% | 7059.9897 | 10
| kVA | IFLC(HV) | CB=1.25*IFLC(HV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  | kVA | IFLC(HV) | CB=1.25*IFLC(HV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  | kVA | IFLC(HV) | CB=1.25*IFLC(HV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  | kVA | IFLC(HV) | CB=1.25*IFLC(HV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA)
TB12= | 500 | 627.5546 | 784.4433 | 800 | MCCB | 5% | 12551.0928 | 25-35 | TB12= | 800 | 1004.0874 | 1255.1093 | 1600 | MCCB | 6% | 16734.7904 | 25-35 | TB12= | 300 | 376.5328 | 470.666 | 500 | MCCB | 4% | 9413.3196 | 15-18 | TB12= | 112.5 | 141.1998 | 176.4997 | 200 | MCCB | 4% | 3529.9949 | 6-10
|  | IFLC(LV) | CB=1.25*IFLC(LV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  |  | IFLC(LV) | CB=1.25*IFLC(LV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  |  | IFLC(LV) | CB=1.25*IFLC(LV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  |  | IFLC(LV) | CB=1.25*IFLC(LV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA)
|  | 1255.1093 | 1568.8866 | 1600 | MCCB | 5% | 25102.1856 | 60 |  |  | 2008.1748 | 2510.2186 | 3000 | MCCB | 6% | 33469.5808 | 60 |  |  | 753.0656 | 941.332 | 1000 | MCCB | 4% | 18826.6392 | 25-35 |  |  | 282.3996 | 352.9995 | 400 | MCCB | 4% | 7059.9897 | 10
| kVA | IFLC(HV) | CB=1.25*IFLC(HV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  | kVA | IFLC(HV) | CB=1.25*IFLC(HV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  | kVA | IFLC(HV) | CB=1.25*IFLC(HV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  | kVA | IFLC(HV) | CB=1.25*IFLC(HV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA)
TB13= | 150 | 188.2664 | 235.333 | 250 | MCCB | 4% | 4706.6598 | 10 | TB13= | 450 | 564.7992 | 705.999 | 800 | MCCB | 5% | 11295.9835 | 15-18 | TB13= | 300 | 376.5328 | 470.666 | 500 | MCCB | 4% | 9413.3196 | 15-18 | TB13= | 600 | 753.0656 | 941.332 | 1000 | MCCB | 5% | 15061.3114 | 25-35
|  | IFLC(LV) | CB=1.25*IFLC(LV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  |  | IFLC(LV) | CB=1.25*IFLC(LV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  |  | IFLC(LV) | CB=1.25*IFLC(LV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  |  | IFLC(LV) | CB=1.25*IFLC(LV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA)
|  | 376.5328 | 470.666 | 500 | MCCB | 4% | 9413.3196 | 15-18 |  |  | 1129.5984 | 1411.9979 | 1600 | MCCB | 5% | 22591.9671 | 25-35 |  |  | 753.0656 | 941.332 | 1000 | MCCB | 4% | 18826.6392 | 25-35 |  |  | 1506.1311 | 1882.6639 | 2000 | MCCB | 5% | 30122.6227 | 60
| kVA | IFLC(HV) | CB=1.25*IFLC(HV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  | kVA | IFLC(HV) | CB=1.25*IFLC(HV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  | kVA | IFLC(HV) | CB=1.25*IFLC(HV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  | kVA | IFLC(HV) | CB=1.25*IFLC(HV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA)
TB14= | 300 | 376.5328 | 470.666 | 500 | MCCB | 4% | 9413.3196 | 15-18 | TB14= | 800 | 1004.0874 | 1255.1093 | 1600 | MCCB | 6% | 16734.7904 | 25-35 | TB14= | 450 | 564.7992 | 705.999 | 800 | MCCB | 5% | 11295.9835 | 15-18 | TB14= | 450 | 564.7992 | 705.999 | 800 | MCCB | 5% | 11295.9835 | 15-18
|  | IFLC(LV) | CB=1.25*IFLC(LV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  |  | IFLC(LV) | CB=1.25*IFLC(LV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  |  | IFLC(LV) | CB=1.25*IFLC(LV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  |  | IFLC(LV) | CB=1.25*IFLC(LV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA)
|  | 753.0656 | 941.332 | 1000 | MCCB | 4% | 18826.6392 | 25-35 |  |  | 2008.1748 | 2510.2186 | 3000 | MCCB | 6% | 33469.5808 | 60 |  |  | 1129.5984 | 1411.9979 | 1600 | MCCB | 5% | 22591.9671 | 25-35 |  |  | 1129.5984 | 1411.9979 | 1600 | MCCB | 5% | 22591.9671 | 25-35
| kVA | IFLC(HV) | CB=1.25*IFLC(HV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  | kVA | IFLC(HV) | CB=1.25*IFLC(HV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  | kVA | IFLC(HV) | CB=1.25*IFLC(HV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  | kVA | IFLC(HV) | CB=1.25*IFLC(HV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA)
TB15= | 600 | 753.0656 | 941.332 | 1000 | MCCB | 5% | 15061.3114 | 25-35 | TB15= | 225 | 282.3996 | 352.9995 | 400 | MCCB | 4% | 7059.9897 | 10 | TB15= | 450 | 564.7992 | 705.999 | 800 | MCCB | 5% | 11295.9835 | 15-18 | TB15= | 500 | 627.5546 | 784.4433 | 800 | MCCB | 5% | 12551.0928 | 25-35
|  | IFLC(LV) | CB=1.25*IFLC(LV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  |  | IFLC(LV) | CB=1.25*IFLC(LV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  |  | IFLC(LV) | CB=1.25*IFLC(LV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  |  | IFLC(LV) | CB=1.25*IFLC(LV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA)
|  | 1506.1311 | 1882.6639 | 2000 | MCCB | 5% | 30122.6227 | 60 |  |  | 564.7992 | 705.999 | 800 | MCCB | 4% | 14119.9794 | 25-35 |  |  | 1129.5984 | 1411.9979 | 1600 | MCCB | 5% | 22591.9671 | 25-35 |  |  | 1255.1093 | 1568.8866 | 1600 | MCCB | 5% | 25102.1856 | 60
| kVA | IFLC(HV) | CB=1.25*IFLC(HV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  | kVA | IFLC(HV) | CB=1.25*IFLC(HV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  | kVA | IFLC(HV) | CB=1.25*IFLC(HV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  | kVA | IFLC(HV) | CB=1.25*IFLC(HV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA)
TB16= | 225 | 282.3996 | 352.9995 | 400 | MCCB | 4% | 7059.9897 | 10 | TBU1= | 2500 | 20.9185 | 26.1481 | 70 | ACB | 6% | 348.6415 | 6 | TBU1= | 2500 | 20.9185 | 26.1481 | 70 | ACB | 6% | 348.6415 | 6 | TB16= | 112.5 | 141.1998 | 176.4997 | 200 | MCCB | 4% | 3529.9949 | 6-10
|  | IFLC(LV) | CB=1.25*IFLC(LV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  |  | IFLC(LV) | CB=1.25*IFLC(LV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  |  | IFLC(LV) | CB=1.25*IFLC(LV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  |  | IFLC(LV) | CB=1.25*IFLC(LV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA)
|  | 564.7992 | 705.999 | 800 | MCCB | 4% | 14119.9794 | 25-35 |  |  | 109.3466 | 136.6833 | 150 | ACB | 6% | 1822.444 | 6-10 |  |  | 109.3466 | 136.6833 | 150 | ACB | 6% | 1822.444 | 6-10 |  |  | 282.3996 | 352.9995 | 400 | MCCB | 4% | 7059.9897 | 10
| kVA | IFLC(HV) | CB=1.25*IFLC(HV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  | kVA | IFLC(HV) | CB=1.25*IFLC(HV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  | kVA | IFLC(HV) | CB=1.25*IFLC(HV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  | kVA | IFLC(HV) | CB=1.25*IFLC(HV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA)
TB17= | 300 | 376.5328 | 470.666 | 500 | MCCB | 4% | 9413.3196 | 15-18 | TBU2= | 2000 | 16.7348 | 20.9185 | 70 | ACB | 6% | 278.9132 | 6 | TBU2= | 2500 | 20.9185 | 26.1481 | 70 | ACB | 6% | 348.6415 | 6 | TBU1= | 2500 | 20.9185 | 26.1481 | 70 | ACB | 6% | 348.6415 | 6
|  | IFLC(LV) | CB=1.25*IFLC(LV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  |  | IFLC(LV) | CB=1.25*IFLC(LV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  |  | IFLC(LV) | CB=1.25*IFLC(LV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) |  |  | IFLC(LV) | CB=1.25*IFLC(LV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA)
|  | 753.0656 | 941.332 | 1000 | MCCB | 4% | 18826.6392 | 25-35 |  |  | 87.4773 | 109.3466 | 110 | ACB | 6% | 1457.9552 | 6-10 |  |  | 109.3466 | 136.6833 | 150 | ACB | 6% | 1822.444 | 6-10 |  |  | 109.3466 | 136.6833 | 150 | ACB | 6% | 1822.444 | 6-10
| kVA | IFLC(HV) | CB=1.25*IFLC(HV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) | [19 empty] | kVA | IFLC(HV) | CB=1.25*IFLC(HV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA)
TB18= | 800 | 1004.0874 | 1255.1093 | 1600 | MCCB | 6% | 16734.7904 | 25-35 | [18 empty] | TBU2= | 2500 | 20.9185 | 26.1481 | 70 | ACB | 6% | 348.6415 | 6
|  | IFLC(LV) | CB=1.25*IFLC(LV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA) | [20 empty] | IFLC(LV) | CB=1.25*IFLC(LV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA)
|  | 2008.1748 | 2510.2186 | 3000 | MCCB | 6% | 33469.5808 | 60 | [20 empty] | 109.3466 | 136.6833 | 150 | ACB | 6% | 1822.444 | 6-10
| kVA | IFLC(HV) | CB=1.25*IFLC(HV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA)
TBU1= | 2000 | 16.7348 | 20.9185 | 70 | ACB | 6% | 278.9132 | 6
|  | IFLC(LV) | CB=1.25*IFLC(LV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA)
|  | 87.4773 | 109.3466 | 110 | ACB | 6% | 1457.9552 | 6-10
| kVA | IFLC(HV) | CB=1.25*IFLC(HV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA)
TBU2= | 1600 | 13.3878 | 16.7348 | 70 | ACB | 6% | 223.1305 | 6
|  | IFLC(LV) | CB=1.25*IFLC(LV) | Standard CB Size | Breaker Type | Impedance | IFAULT | KAIC Rating(kA)
|  | 69.9819 | 87.4773 | 90 | ACB | 6% | 1166.3642 | 6

## LOOKUP VALUES (hidden)
|  |  | 100 | 4%
70 | 70 |  | 300 | 4% | 0.25 | 250 | 6
80 | 80 |  | 600 | 5% | 1.25 | 1250 | 6
90 | 90 |  | 2500 | 6% | 3.75 | 3750 | 6-10
100 | 100 |  | 5000 | 6.5% | 7.5 | 7500 | 10
110 | 110 |  | 7500 | 7.5% | 12.5 | 12500 | 15-18
125 | 125 |  | 10000 | 8.5% | 25 | 25000 | 25-35
150 | 150 |  | 1000000000 | 9.5% | 50 | 50000 | 60
175 | 175 |  |  |  | 81.25 | 81250 | 65
200 | 200 |  |  |  | 106.25 | 106250 | 85
225 | 225 |  |  |  | 125 | 125000 | 100
250 | 250 |  |  |  | 156.25 | 156250 | 125
300 | 300 |  |  |  | 187.5 | 187500 | 150
350 | 350 |  |  |  | 250 | 250000 | 200-250
400 | 400
450 | 450
500 | 500
600 | 600
700 | 700
800 | 800
900 | 900
1000 | 1000
1200 | 1200
1600 | 1600
2000 | 2000
2500 | 2500
3000 | 3000
4000 | 4000
5000 | 5000
6000 | 6000
Column1 |  | Base Load
Base load |  | Capacity Factor
capacity factor |  | Connecting Load
connecting load |  | Demand Factor
demand factor |  | Diversity Factor
diversity factor |  | Geographic Location
Geographic location |  | Load Curve
load curve |  | Load Estimation
load estimation |  | Load Factor
load factor |  | Maximum Demand
maximum demand |  | Motor Efficiency
motor efficiency |  | Peak Load
peak load |  | Percentage Impedance
percentage impedance |  | Plan Use Factor
plan use factor |  | Power Load
power load |  | Power Plant
power plant |  | Substation
substation |  | Transformer
transformer